## Data Log Chiller
DOP CHILLER LOG SHEET
Tgl | jam | load comp | expan | temp suction EH | press. cond | press. evap | Temp. water inlet evap | Temp. water inlet cond | temp. water outlet evap | temp. water outlet cond | temp. delivery gas | temp. suction gas | temp. cond saturated | temp. evap saturated | curent motor | running hour | Temp Approach Cond | Temp Approach Evap | Press. water in evap | Press. water outlet evap | Press. water in Cond | Press. water outlet cond | Remark
[5 empty] | (0.7-1.1) | [11 empty] | (0-4) | 0
|  | % | P | °C | Mpa | MPa | °C | °C | °C | °C | °C | °C | °C | °C | A | H | °C | °C | Bar | Bar | Bar | Bar
2025-07-04 | 10:00 | 60 | 253 | 4 | 0.98 | 0.34 | 17.9 | 28.4 | 14.8 | 30.6 | 64.5 | 17.6 | 42.5 | 12 | 28 | xx | 11.9 | 2.8 | xx | xx | xx | xx
2025-07-04 | 14:00 | 65 | 280 | 4 | 1.06 | 0.33 | 17.2 | 28.2 | 13.6 | 31.1 | 61.4 | 14.5 | 45.3 | 11.3 | xx | xx | 14.2 | 2.3 | xx | xx | xx | xx
2025-07-05 | 9:00 | 55 | 260 | 4 | 1.01 | 0.34 | 18.1 | 27.7 | 14.6 | 30.2 | 60.6 | 16.3 | 43.2 | 12 | 26.8 | 10285 | 13 | 2.6 | xx | xx | xx | xx
2025-07-05 | 12:00 | 65 | 287 | 4 | 1.06 | 0.33 | 17.6 | 28.1 | 13.9 | 30.8 | 60.7 | 15.1 | 45.3 | 11.3 | 29.7 | 10288 | 14.5 | 2.6 | xx | xx | xx | xx
2025-07-05 | 15:00 | 40 | 223 | 4 | 0.93 | 0.32 | 17.4 | 27.4 | 14.3 | 29.4 | 59.5 | 12.6 | 40.8 | 11.3 | 24.2 | 10291 | 11.4 | 3 | xx | xx | xx | xx
2025-07-06 | 9:00 | 65 | 284 | 4 | 1.08 | 0.33 | 17.6 | 28.4 | 13.9 | 31.2 | 61.9 | 15.6 | 45.9 | 11.3 | 30.1 | 10309 | 14.7 | 2.6 | xx | xx | xx | xx
2025-07-06 | 13:00 | 65 | 283 | 4 | 1.08 | 0.33 | 17.3 | 29.8 | 13.7 | 31.5 | 61.3 | 14.8 | 45.9 | 11.3 | 30.1 | 10312 | 14.4 | 2.4 | 4 | 3.25 | 2.2 | 1.3
2025-07-06 | 15:00 | 65 | 296 | 4 | 1.03 | 0.33 | 17.6 | 26.8 | 13.9 | 29.6 | 59.2 | 13.4 | 44.3 | 11.3 | 29.1 | 10315 | 14.7 | 2.6 | 4 | 3.2 | 2.2 | 1.4
2025-07-07 | 9:00 | 75 | 368 | 4 | 1.11 | 0.32 | 17.2 | 27.8 | 13.2 | 30.9 | 62.2 | 14 | 46.9 | 10.6 | 33.8 | 10333 | 16 | 2.6 | 4 | 3.3 | 2.2 | 1.4
2025-07-07 | 13:00 | 70 | 297 | 4 | 1.07 | 0.32 | 17 | 27.8 | 13.2 | 30.5 | 61.3 | 14.3 | 45.6 | 10.6 | 31.1 | 10336 | 15.1 | 2.6 | 4 | 3.25 | 2.6 | 1.4
2025-07-07 | 15:00 | 70 | 294 | 4 | 1.07 | 0.32 | 16.9 | 28 | 13.1 | 30.5 | 60.7 | 14 | 45.6 | 10.6 | 30.9 | 10338 | 15.1 | 2.5 | 4 | 3.25 | 2.6 | 1.4
2025-07-10 | 9:00 | 55 | 273 | 4 | 1.02 | 0.34 | 18 | 27.3 | 14.4 | 29.7 | 60.2 | 16.3 | 43.9 | 12 | 27.4 | 10405 | 14.2 | 2.4 | 4 | 3.25 | 2.6 | 1.5
2025-07-10 | 13:00 | 60 | 269 | 4 | 1.05 | 0.34 | 17.7 | 28.8 | 14.2 | 31.2 | 60.9 | 15.8 | 44.9 | 12 | 28.7 | 10409 | 13.7 | 2.2 | 4 | 3.2 | 2.6 | 1.4
2025-07-10 | 15:00 | 45 | 261 | 4 | 1 | 0.34 | 18 | 27.7 | 14.5 | 30 | 60.5 | 16.3 | 43.6 | 12 | 25.4 | 10411 | 13.6 | 2.5 | 4 | 3.25 | 2.6 | 1.4
2025-07-11 | 9:00 | 60 | 271 | 4 | 1.03 | 0.33 | 17.7 | 27.4 | 14.2 | 29.9 | 60.4 | 15.8 | 44.3 | 11.3 | 28 | 10428 | 14.4 | 2.9 | 4 | 3.25 | 2.25 | 1.4
2025-07-11 | 13:00 | 60 | 270 | 4 | 1.03 | 0.33 | 17.3 | 27.5 | 14.3 | 29.4 | 60.7 | 15.8 | 44.2 | 11.3 | 27.5 | 10432 | 14.8 | 3 | 4 | 3.25 | 2.25 | 1.4
2025-07-11 | 15:00 | 55 | 261 | 4 | 1 | 0.34 | 18 | 27.7 | 14.5 | 30 | 60.5 | 16.3 | 43.6 | 12 | 27.4 | 10434 | 13.6 | 2.5 | 4 | 3.25 | 2.6 | 1.4
Cleaning mekanical
14 juli 2025 | 14:00 | 50 | 323 | 7 | 0.8 | 0.32 | 16.6 | 28.8 | 13.3 | 32.3 | 51.5 | 11.1 | 34.6 | 11.3 | 20.9 | 10445 | 2.3 | 2 | 4 | 3.25 | 1.3 | 1
20 juli 2025 | 9:00 | 30 | 269 | 4 | 0.73 | 0.37 | 19.4 | 27.3 | 16.3 | 29.6 | 51.1 | 17.3 | 32.9 | 14 | 20.3 | 10452 | 3.3 | 2.3 | 4 | 3.25 | 2 | 1.2
20 juli 2025 | 10:00 | 45 | 367 | 4 | 0.82 | 0.36 | 20.4 | 29.7 | 16.1 | 32.8 | 50.2 | 17.6 | 36.6 | 13.3 | 22.1 | 10453 | 3.8 | 2.8 | 4 | 3.3 | 2.2 | 1.3
21 juli 2025 | 9:00 | 35 | 272 | 4 | 0.73 | 0.36 | 19 | 27.1 | 15.9 | 29.4 | 50.8 | 17 | 32.9 | 13.3 | 20.7 | 10476 | 3.5 | 2.6 | 4 | 3.3 | 2.2 | 1.3
21 juli 2025 | 15:00 | 55 | 316 | 4 | 0.8 | 0.35 | 19.5 | 29.1 | 15.3 | 31.9 | 50.4 | 15.7 | 35.8 | 12 | 22.5 | 10483 | 3.9 | 3.3 | 4 | 3.2 | 2.2 | 1.2
22 juli 2025 | 8:00 | 35 | 268 | 4 | 0.73 | 0.35 | 18.5 | 26.8 | 15.4 | 29.6 | 50.7 | 17.2 | 32.5 | 12.7 | 20.5 | 10498 | 2.9 | 2.7 | 4 | 3.2 | 2.2 | 1.3
22 juli 2025 | 1:00 | 55 | 279 | 4 | 0.78 | 0.35 | 19.7 | 28.7 | 16.1 | 31.2 | 51.5 | 18 | 35 | 13.3 | 23.9 | 10503 | 3.8 | 2.8 | 4 | 3.2 | 2.2 | 1.3
23 juli 2025 | 8:00 | 35 | 263 | 4 | 0.75 | 0.36 | 19.1 | 27.7 | 15.9 | 30 | 52.4 | 17.7 | 34.2 | 13.3 | 20.9 | 10523 | 4.2 | 2.6 | 4 | 3.2 | 2 | 1.2
23 juli 2025 | 1:00 | 45 | 278 | 4 | 0.79 | 0.35 | 18.9 | 28.8 | 15.4 | 31.2 | 51.3 | 16.7 | 35.4 | 12.7 | 22.3 | 10527 | 4.2 | 2.7 | 4 | 3.2 | 2.2 | 1.3
24 juli 2025 | 9:00 | 60 | 361 | 4 | 0.84 | 0.36 | 20.6 | 29.6 | 16.3 | 32.5 | 51.3 | 18 | 37.4 | 13.3 | 24.4 | 10548 | 4.9 | 3 | 4 | 3.2 | 2.2 | 1.3
24 juli 2025 | 15:00 | 50 | 246 | 4 | 0.8 | 0.35 | 19.5 | 28.5 | 15.8 | 31.1 | 52 | 17.1 | 35.8 | 12.7 | 22.9 | 10556 | 4.7 | 3.1 | 4 | 3.2 | 2.2 | 1.3
25 juli 2025 | 8:00 | 35 | 262 | 4 | 0.78 | 0.37 | 19.8 | 28.4 | 16.5 | 30.5 | 53.2 | 18.4 | 35 | 14 | 21.3 | 10571 | 4.5 | 2.5 | 4 | 3.3 | 2.2 | 1.3
25 juli 2025 | 16:00 | 65 | 374 | 4 | 0.84 | 0.35 | 19.3 | 29 | 15.4 | 31.7 | 50.7 | 14.6 | 35.8 | 9.1 | 21.5 | 10574 | 4.1 | 6.3 | 4 | 3.3 | 2.2 | 1.3
26 juli 2025 | 8:00 | 30 | 247 | 4 | 0.76 | 0.36 | 18.9 | 27.3 | 15.9 | 29.4 | 53.3 | 17.5 | 34.2 | 13.3 | 20.7 | 10595 | 4.8 | 2.6 | 4 | 3.3 | 2 | 1.3
26 juli 2025 | 16:00 | 60 | 315 | 4 | 0.83 | 0.36 | 20 | 29.1 | 16 | 32.9 | 51.8 | 16.8 | 37 | 13.3 | 24.4 | 10603 | 4.1 | 2.7 | 4 | 3.2 | 2.2 | 1.3
Cleaning Chemical
03 Agst 2025 | 14:00 | 100 | 656 | 7 | 0.87 | 0.31 | 20.6 | 28.5 | 14.7 | 34 | 55.1 | 20.6 | 37.8 | 11.3 | 31.1 | 10690 | 3.8 | 3.4 | 4 | 3.2 | 1.7 | 1.2
03 Agst 2025 | 14:00 | 70 | 656 | 4 | 0.8 | 0.36 | 18.4 | 20.5 | 14.7 | 32 | 52.6 | 16 | 35.5 | 14 | 23.1 | 10690 | 3.5 | 0.7 | 4 | 3.2 | 1.7 | 1.2
7 Agst 2025 | 16:00 | 60 | 651 | 4 | 0.8 | 0.37 | 17.3 | 29.4 | 14.6 | 32.2 | 49.6 | 15 | 35 | 13.3 | 20.3 | 10696 | 2.8 | 1.3 | 4 | 3.3 | 1.6 | 1.1 | startup
8 Agst 2025 | 16:00 | 60 | 488 | 4 | 0.76 | 0.36 | 20.1 | 27.5 | 16 | 30.5 | 49.6 | 17.7 | 34.2 | 13.3 | 23.9 | 10698 | 3.7 | 2.7 | 4 | 3.3 | 2.2 | 1.3
9 Agst 2025 | 8:30 | 60 | 320 | 4 | 0.76 | 0.36 | 20 | 28.4 | 16.1 | 31.1 | 49.6 | 17.7 | 34.2 | 13.3 | 23.5 | 10722 | 3.1 | 2.8 | 4 | 3.3 | 2.2 | 1.3
9 Agst 2025 | 16:00 | 45 | 376 | 4 | 0.78 | 0.37 | 20.7 | 29 | 16.4 | 31.7 | 49.6 | 17.7 | 35 | 13.3 | 23.5 | 10736 | 3.3 | 3.1 | 4 | 3.3 | 2.2 | 1.3
10 Agst 2025 | 8:30 | 35 | 276 | 4 | 0.71 | 0.35 | 18.6 | 26.7 | 15.4 | 28.8 | 49.8 | 16.8 | 32 | 12.7 | 20.5 | 10736 | 3.2 | 2.7 | 4 | 3.3 | 2.2 | 1.3
14 Agst 2025 | 8:30 | 55 | 300 | 4 | 0.74 | 0.36 | 19.4 | 27.5 | 15.8 | 29.9 | 49.8 | 16.9 | 33.3 | 12.7 | 21.7 | 10808 | 3.4 | 3.1 | 4 | 3.3 | 2.2 | 1.3
914.5228

## Perhitungan h1-h4 rev
[6 empty] | p2 | p1 | t1 | t2 | t3
Sebelum Mechanical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C)
| In | Out | In | Out
45% | 18 | 14.5 | 27.7 | 30 | 25.4 | 1 | 0.34 | 16.3 | 60.5 | 43.6
55% | 18 | 14.4 | 27.3 | 29.7 | 27.4 | 1.02 | 0.34 | 16.3 | 60.2 | 43.9
60% | 17.9 | 14.8 | 28.4 | 30.6 | 28 | 0.98 | 0.34 | 17.6 | 64.5 | 42.5
Load 45%
Diket | T1 = | 16.3 | (Saturated vapor) |  |  |  | h1 = | 259.672 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 293.9235 | kJ/kg
| T2 = | 60.5 | (Superheated) |  |  |  | h3 = | 113.696 | kJ/kg
| P2 = | 1 | Mpa |  |  |  | h4 = | 113.696 | kJ/kg
| T3 = | 43.6 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 16,3 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 34.2515 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
| Menggunakan Interpolasi | [6 empty] | Qcond = | h2 - h3
[9 empty] | 180.2275 | kJ/kg
c. Kalor Evaporator
[8 empty] | Qevap = | h1 - h4
|  | h1 = | 259.672 | kJ/kg |  |  |  |  | 145.976 | kJ/kg
T2 = 60,5 C | [6 empty] | d. COP
P2 = 1 Mpa | Tabel Superheated Refrigerant R134a 1 MPa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 60 | C | 293.4 | kJ/kg |  |  |  | 4.2619
|  | 70 | C | 303.87 | kJ/kg
|  | h2 = | 293.9235 | kJ/kg
T3 = 43,6 | Temp | 42 | C | 111.28 | kJ/kg
|  | 44 | C | 114.3 | kJ/kg
|  | h3 = | 113.696 | kJ/kg
|  | h4 = | 113.696 | kJ/kg
Load 55%
Diket | T1 = | 16.3 | (Saturated vapor) |  |  |  | h1 = | 259.672 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 293.9824 | kJ/kg
| T2 = | 60.2 | (Superheated) |  |  |  | h3 = | 114.149 | kJ/kg
| P2 = | 1.02 | Mpa |  |  |  | h4 = | 114.149 | kJ/kg
| T3 = | 43.9 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 16,3 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 34.3104 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
| Menggunakan Interpolasi | [6 empty] | Qcond = | h2 - h3
[9 empty] | 179.8334 | kJ/kg
c. Kalor Evaporator
[8 empty] | Qevap = | h1 - h4
|  | h1 = | 259.672 | kJ/kg |  |  |  |  | 145.523 | kJ/kg
T2 = 60,2 C | [6 empty] | d. COP
P2 = 1,02 Mpa | [7 empty] | COP = | Qevap/Wcomp
| Tabel Superheated Refrigerant R134a 1 MPa | [7 empty] | 4.2414
| Temp | 60 | C | 293.4 | kJ/kg
|  | 70 | C | 303.87 | kJ/kg
|  | h 1 Mpa | 293.6094 | kJ/kg
Tabel Superheated Refrigerant R134a 1 MPa
| Temp | 60 | C | 289.66 | kJ/kg
|  | 70 | C | 300.63 | kJ/kg
|  | h 1,2 Mpa | 289.8794 | kJ/kg
Interpolasi P2 1,02 MPa :
|  | h2 = | 293.9824 | kJ/kg
T3 = 43,9 | Temp | 42 | C | 111.28 | kJ/kg
|  | 44 | C | 114.3 | kJ/kg
|  | h3 = | 114.149 | kJ/kg
|  | h4 = | 114.149 | kJ/kg
Load 60%
Diket | T1 = | 17.6 | (Saturated vapor) |  |  |  | h1 = | 260.374 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 298.4426 | kJ/kg
| T2 = | 64.5 | (Superheated) |  |  |  | h3 = | 112.035 | kJ/kg
| P2 = | 0.98 | Mpa |  |  |  | h4 = | 112.035 | kJ/kg
| T3 = | 42.5 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 17,6 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 38.0686 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
| Menggunakan Interpolasi | [6 empty] | Qcond = | h2 - h3
[9 empty] | 186.4076 | kJ/kg
c. Kalor Evaporator
[8 empty] | Qevap = | h1 - h4
|  | h1 = | 260.374 | kJ/kg |  |  |  |  | 148.339 | kJ/kg
T2 = 64,5 C | [6 empty] | d. COP
P2 = 0,98 Mpa | [7 empty] | COP = | Qevap/Wcomp
| Tabel Superheated Refrigerant R134a 0,90 MPa | [7 empty] | 3.8966
| Temp | 60 | C | 295.15 | kJ/kg
|  | 70 | C | 305.41 | kJ/kg
|  | h 0,90 Mpa | 299.767 | kJ/kg
Tabel Superheated Refrigerant R134a 1 MPa
| Temp | 60 | C | 293.4 | kJ/kg
|  | 70 | C | 303.87 | kJ/kg
|  | h 0,80 Mpa | 298.1115 | kJ/kg
Interpolasi P2 0,98 MPa :
|  | h2 = | 298.4426 | kJ/kg
T3 = 42,5 C | Temp | 42 | C | 111.28 | kJ/kg
|  | 44 | C | 114.3 | kJ/kg
|  | h3 = | 112.035 | kJ/kg
|  | h4 = | 112.035 | kJ/kg
Sesudah Mechanical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C)
| In | Out | In | Out
45% | 20.4 | 16:01 | 29.7 | 32.8 | 22.1 | 0.82 | 0.36 | 17.6 | 50.2 | 36.6
55% | 19.7 | 16.1 | 28.7 | 31.2 | 23.9 | 0.78 | 0.35 | 18 | 51.5 | 35
60% | 20 | 16 | 29.1 | 32.9 | 24.4 | 0.83 | 0.36 | 16.8 | 51.8 | 37
Load 45%
Diket | T1 = | 17.6 | (Saturated vapor) |  |  |  | h1 = | 260.374 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 286.5292 | kJ/kg
| T2 = | 50.2 | (Superheated) |  |  |  | h3 = | 103.228 | kJ/kg
| P2 = | 0.82 | Mpa |  |  |  | h4 = | 103.228 | kJ/kg
| T3 = | 36.6 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 17,6 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 26.1552 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h1 = | 260.374 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 50,2 C | [8 empty] | 183.3012 | kJ/kg
P2 = 0,82 | Tabel Superheated Refrigerant R134a 0,8 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 50 | C | 286.71 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 60 | C | 296.82 | kJ/kg |  |  |  | 157.146 | kJ/kg
|  | h 0,80 Mpa | 286.9122 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,9 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 50 | C | 284.79 | kJ/kg |  |  |  | 6.0082
|  | 60 | C | 295.15 | kJ/kg
|  | h 0,90 Mpa | 284.9972 | kJ/kg
Interpolasi P2 0,82 Mpa :
|  | h2 = | 286.5292 | kJ/kg
T3 = 36,6 C | Temp | 36 | C | 102.34 | kJ/kg
|  | 38 | C | 105.3 | kJ/kg
|  | h3 = | 103.228 | kJ/kg
|  | h4 = | 103.228 | kJ/kg
Load 55%
Diket | T1 = | 18 | (Saturated vapor) |  |  |  | h1 = | 260.59 | kJ/kg
| P1 = | 0.35 | Mpa |  |  |  | h2 = | 288.5862 | kJ/kg
| T2 = | 51.5 | (Superheated) |  |  |  | h3 = | 100.875 | kJ/kg
| P2 = | 0.78 | Mpa |  |  |  | h4 = | 100.875 | kJ/kg
| T3 = | 35 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 18 C | Temp | 18 | C | 260.59 | kJ/kg |  |  |  | 27.9962 | kJ/kg
|  | h1 = | 260.59 | kJ/kg |  |  | b. Kalor Kondensor
T2 = 51,5 C | [7 empty] | Qcond = | h2 - h3
P2 = 0,78 Mpa | Menggunakan Interpolasi | [7 empty] | 187.7112 | kJ/kg
c. Kalor Evaporator
[8 empty] | Qevap = | h1 - h4
[9 empty] | 159.715 | kJ/kg
| Tabel Superheated Refrigerant R134a 0,70 Mpa | [5 empty] | d. COP
| Temp | 50 | C | 288.54 | kJ/kg |  |  | COP = | Qevap/Wcomp
|  | 60 | C | 298.44 | kJ/kg |  |  |  | 5.7049
|  | h 0,70 Mpa | 290.025 | kJ/kg
Tabel Superheated Refrigerant R134a 0,80 Mpa
| Temp | 50 | C | 286.71 | kJ/kg
|  | 60 | C | 296.82 | kJ/kg
|  | h 0,80 Mpa | 288.2265 | kJ/kg
Interpolasi P2 0,78 Mpa :
|  | h2 = | 288.5862 | kJ/kg
T3 = 35 C | Temp | 34 | C | 99.41 | kJ/kg
|  | 36 | C | 102.34 | kJ/kg
|  | h3 = | 100.875 | kJ/kg
|  | h4 = | 100.875 | kJ/kg
Load 60%
Diket | T1 = | 16.8 | (Saturated vapor) |  |  |  | h1 = | 259.942 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 287.9673 | kJ/kg
| T2 = | 51.8 | (Superheated) |  |  |  | h3 = | 103.82 | kJ/kg
| P2 = | 0.83 | Mpa |  |  |  | h4 = | 103.82 | kJ/kg
| T3 = | 37 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 16,8 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 28.0253 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h1 = | 259.942 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 51,8 C | [8 empty] | 184.1473 | kJ/kg
P2 = 0,83 | Tabel Superheated Refrigerant R134a 0,8 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 50 | C | 286.71 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 60 | C | 296.82 | kJ/kg |  |  |  | 156.122 | kJ/kg
|  | h 0,80 Mpa | 288.5298 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,9 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 50 | C | 284.79 | kJ/kg |  |  |  | 5.5708
|  | 60 | C | 295.15 | kJ/kg
|  | h 0,90 Mpa | 286.6548 | kJ/kg
Interpolasi P2 0,83 Mpa :
|  | h2 = | 287.9673 | kJ/kg
T3 = 37 C | Temp | 36 | C | 102.34 | kJ/kg
|  | 38 | C | 105.3 | kJ/kg
|  | h3 = | 103.82 | kJ/kg
|  | h4 = | 103.82 | kJ/kg
Sesudah Chemical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C)
| In | Out | In | Out
45% | 20.7 | 16.4 | 29 | 31.7 | 23.5 | 0.78 | 0.37 | 17.7 | 49.6 | 35
55% | 19.4 | 15.8 | 27.5 | 29.9 | 21.7 | 0.74 | 0.36 | 16.9 | 49.8 | 33.3
60% | 20.1 | 16 | 27.5 | 30.5 | 23.9 | 0.76 | 0.36 | 17.7 | 49.6 | 34.2
Load 45%
Diket | T1 = | 17.7 | (Saturated vapor) |  |  |  | h1 = | 260.428 | kJ/kg
| P1 = | 0.37 | Mpa |  |  |  | h2 = | 286.6684 | kJ/kg
| T2 = | 49.6 | (Superheated) |  |  |  | h3 = | 100.875 | kJ/kg
| P2 = | 0.78 | Mpa |  |  |  | h4 = | 100.875 | kJ/kg
| T3 = | 35 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 17,7 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 26.2404 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h1 = | 260.428 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,6 C | [8 empty] | 185.7934 | kJ/kg
P2 = 0,78 | Tabel Superheated Refrigerant R134a 0,7 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 40 | C | 278.59 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 288.54 | kJ/kg |  |  |  | 159.553 | kJ/kg
|  | h 0,70 Mpa | 288.142 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,8 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 40 | C | 276.46 | kJ/kg |  |  |  | 6.0804
|  | 50 | C | 286.71 | kJ/kg
|  | h 0,80 Mpa | 286.3 | kJ/kg
Interpolasi P2 0,78 Mpa :
|  | h2 = | 286.6684 | kJ/kg
T3 = 35 C | Temp | 34 | C | 99.41 | kJ/kg
|  | 36 | C | 102.34 | kJ/kg
|  | h3 = | 100.875 | kJ/kg
|  | h4 = | 100.875 | kJ/kg
Load 55%
Diket | T1 = | 16.9 | (Saturated vapor) |  |  |  | h1 = | 259.996 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 287.6066 | kJ/kg
| T2 = | 49.8 | (Superheated) |  |  |  | h3 = | 98.388 | kJ/kg
| P2 = | 0.74 | Mpa |  |  |  | h4 = | 98.388 | kJ/kg
| T3 = | 33.3 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 16,9 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 27.6106 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h1 = | 259.996 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,8 C | [8 empty] | 189.2186 | kJ/kg
P2 = 0,74 | Tabel Superheated Refrigerant R134a 0,7 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 40 | C | 278.59 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 288.54 | kJ/kg |  |  |  | 161.608 | kJ/kg
|  | h 0,70 Mpa | 288.341 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,8 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 40 | C | 276.46 | kJ/kg |  |  |  | 5.8531
|  | 50 | C | 286.71 | kJ/kg
|  | h 0,80 Mpa | 286.505 | kJ/kg
Interpolasi P2 0,74 Mpa :
|  | h2 = | 287.6066 | kJ/kg
T3 = 33,3 C | Temp | 32 | C | 96.49 | kJ/kg
|  | 34 | C | 99.41 | kJ/kg
|  | h3 = | 98.388 | kJ/kg
|  | h4 = | 98.388 | kJ/kg
Load 60%
Diket | T1 = | 17.7 | (Saturated vapor) |  |  |  | h1 = | 259.672 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 287.221 | kJ/kg
| T2 = | 49.6 | (Superheated) |  |  |  | h3 = | 98.959 | kJ/kg
| P2 = | 0.76 | Mpa |  |  |  | h4 = | 98.959 | kJ/kg
| T3 = | 34.2 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 17,7 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 27.549 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h1 = | 259.672 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,6 C | [8 empty] | 188.262 | kJ/kg
P2 = 0,76 | Tabel Superheated Refrigerant R134a 0,7 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 40 | C | 278.59 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 288.54 | kJ/kg |  |  |  | 160.713 | kJ/kg
|  | h 0,70 Mpa | 288.142 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,8 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 40 | C | 276.46 | kJ/kg |  |  |  | 5.8337
|  | 50 | C | 286.71 | kJ/kg
|  | h 0,80 Mpa | 286.3 | kJ/kg
Interpolasi P2 0,75 Mpa :
|  | h2 = | 287.221 | kJ/kg
T3 = 34,2 C | Temp | 34 | C | 98.67 | kJ/kg
|  | 36 | C | 101.56 | kJ/kg
|  | h3 = | 98.959 | kJ/kg
|  | h4 = | 98.959 | kJ/kg
Kondisi | Load (%) | Enthalpy kJ/kg | [6 empty] | COP
|  | h1 | h2 | h3 | h4 | Wcomp | Qcond | Qevap
Sebelum Mechanical Cleaning | 45 | 259.672 | 293.9235 | 113.696 | 113.696 | 34.2515 | 180.2275 | 145.976 | 4.2619
| 55 | 259.672 | 293.9824 | 114.149 | 114.149 | 34.3104 | 179.8334 | 145.523 | 4.2414
| 60 | 260.374 | 298.4426 | 112.035 | 112.035 | 38.0686 | 186.4076 | 148.339 | 3.8966
Sesudah Mechanical Cleaning | 45 | 260.374 | 286.5292 | 103.228 | 103.228 | 26.1552 | 183.3012 | 157.146 | 6.0082
| 55 | 260.59 | 288.5862 | 100.875 | 100.875 | 27.9962 | 187.7112 | 159.715 | 5.7049
| 60 | 259.942 | 287.9673 | 103.82 | 103.82 | 28.0253 | 184.1473 | 156.122 | 5.5708
Sesudah Chemical Cleaning | 45 | 260.428 | 286.6684 | 100.875 | 100.875 | 26.2404 | 185.7934 | 159.553 | 6.0804
| 55 | 259.996 | 287.6066 | 98.388 | 98.388 | 27.6106 | 189.2186 | 161.608 | 5.8531
| 60 | 259.672 | 287.221 | 98.959 | 98.959 | 27.549 | 188.262 | 160.713 | 5.8337

## Perhitungan h1-h4 rev (2)
[6 empty] | p2 | p1 | t1 | t2 | t3
Sebelum Mechanical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C) | Temp. evap saturated (°C)
| In | Out | In | Out
45% | 18 | 14.5 | 27.7 | 30 | 25.4 | 1 | 0.34 | 16.3 | 60.5 | 43.6 | 12
55% | 18 | 14.4 | 27.3 | 29.7 | 27.4 | 1.02 | 0.34 | 16.3 | 60.2 | 43.9 | 12
60% | 17.9 | 14.8 | 28.4 | 30.6 | 28 | 0.98 | 0.34 | 17.6 | 64.5 | 42.5 | 12
Load 45%
Diket | T1 = | 16.3 | (Superheated vapor) |  |  |  | h1 = | 264.8282 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 293.9235 | kJ/kg
| T2 = | 60.5 | (Superheated vapor) |  |  |  | h3 = | 113.696 | kJ/kg
| P2 = | 1 | Mpa |  |  |  | h4 = | 113.696 | kJ/kg
| T3 = | 43.6 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
[8 empty] | Wcomp = | h2 - h1
[9 empty] | 29.0953 | kJ/kg
b. Kalor Kondensor
T1 = 16,3 C | Dengan menggunakan table A-13 Refirgerant R134a P = 0,32 Mpa | [6 empty] | Qcond = | h2 - h3
P1 = 0,34 Mpa | Temp | 10 | C | 258.7 | kJ/kg |  |  |  | 180.2275 | kJ/kg
|  | 20 | C | 267.67 | kJ/kg |  | c. Kalor Evaporator
|  | h 0,32 Mpa | 264.3511 | kJ/kg |  |  |  | Qevap = | h1 - h4
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,4 Mpa | [7 empty] | 151.1322 | kJ/kg
| Temp | 10 | C | 256.59 | kJ/kg |  | d. COP
|  | 20 | C | 265.88 | kJ/kg |  |  | COP = | Qevap/Wcomp
|  | h 0,4 Mpa | 262.4427 | kJ/kg |  |  |  |  | 5.1944
Interpolasi P1 0,34 Mpa
|  | h1 = | 264.8282 | kJ/kg
T2 = 60,5 C
P2 = 1 Mpa | Tabel Superheated Refrigerant R134a 1 MPa
| Temp | 60 | C | 293.4 | kJ/kg
|  | 70 | C | 303.87 | kJ/kg
|  | h2 = | 293.9235 | kJ/kg
T3 = 43,6 | Temp | 42 | C | 111.28 | kJ/kg
|  | 44 | C | 114.3 | kJ/kg
|  | h3 = | 113.696 | kJ/kg
|  | h4 = | 113.696 | kJ/kg
Load 55%
Diket | T1 = | 16.3 | (Superheated vapor) |  |  |  | h1 = | 264.8282 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 293.9824 | kJ/kg
| T2 = | 60.2 | (Superheated) |  |  |  | h3 = | 114.149 | kJ/kg
| P2 = | 1.02 | Mpa |  |  |  | h4 = | 114.149 | kJ/kg
| T3 = | 43.9 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
[8 empty] | Wcomp = | h2 - h1
[9 empty] | 29.1542 | kJ/kg
T1 = 16,3 C | Dengan menggunakan table A-13 Refirgerant R134a P = 0,32 Mpa | [5 empty] | b. Kalor Kondensor
P1 = 0,34 Mpa | Temp | 10 | C | 258.7 | kJ/kg |  |  | Qcond = | h2 - h3
|  | 20 | C | 267.67 | kJ/kg |  |  |  | 179.8334 | kJ/kg
|  | h 0,32 Mpa | 264.3511 | kJ/kg |  |  | c. Kalor Evaporator
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,4 Mpa | [6 empty] | Qevap = | h1 - h4
| Temp | 10 | C | 256.59 | kJ/kg |  |  |  | 150.6792 | kJ/kg
|  | 20 | C | 265.88 | kJ/kg |  | d. COP
|  | h 0,4 Mpa | 262.4427 | kJ/kg |  |  |  | COP = | Qevap/Wcomp
| Interpolasi P1 0,34 Mpa | [7 empty] | 5.1684
|  | h1 = | 264.8282 | kJ/kg
T2 = 60,2 C
P2 = 1,02 Mpa
Tabel Superheated Refrigerant R134a 1 MPa
| Temp | 60 | C | 293.4 | kJ/kg
|  | 70 | C | 303.87 | kJ/kg
|  | h 1 Mpa | 293.6094 | kJ/kg
Tabel Superheated Refrigerant R134a 1 MPa
| Temp | 60 | C | 289.66 | kJ/kg
|  | 70 | C | 300.63 | kJ/kg
|  | h 1,2 Mpa | 289.8794 | kJ/kg
Interpolasi P2 1,02 MPa :
|  | h2 = | 293.9824 | kJ/kg
T3 = 43,9 | Temp | 42 | C | 111.28 | kJ/kg
|  | 44 | C | 114.3 | kJ/kg
|  | h3 = | 114.149 | kJ/kg
|  | h4 = | 114.149 | kJ/kg
Load 60%
Diket | T1 = | 17.6 | (Superheated vapor) |  |  |  | h1 = | 259.5009 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 298.4426 | kJ/kg
| T2 = | 64.5 | (Superheated) |  |  |  | h3 = | 112.035 | kJ/kg
| P2 = | 0.98 | Mpa |  |  |  | h4 = | 112.035 | kJ/kg
| T3 = | 42.5 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,32 Mpa | [6 empty] | Wcomp = | h2 - h1
T1 = 17,6 C | Temp | 10 | C | 259.51 | kJ/kg |  |  |  | 38.9417 | kJ/kg
P1 = 0,34 Mpa |  | 20 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h 0,32 Mpa | 260.3308 | kJ/kg |  |  |  | Qcond = | h2 - h3
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,4 Mpa | [7 empty] | 186.4076 | kJ/kg
| Temp | 10 | C | 256.59 | kJ/kg |  | c. Kalor Evaporator
|  | 20 | C | 265.88 | kJ/kg |  |  | Qevap = | h1 - h4
|  | h 0,4 Mpa | 263.6504 | kJ/kg |  |  |  |  | 147.4659 | kJ/kg
| Interpolasi P1 0,34 Mpa | [5 empty] | d. COP
|  | h1 = | 259.5009 | kJ/kg |  |  |  | COP = | Qevap/Wcomp
T2 = 64,5 C | [8 empty] | 3.7868
P2 = 0,98 Mpa
Tabel Superheated Refrigerant R134a 0,90 MPa
| Temp | 60 | C | 295.15 | kJ/kg
|  | 70 | C | 305.41 | kJ/kg
|  | h 0,90 Mpa | 299.767 | kJ/kg
Tabel Superheated Refrigerant R134a 1 MPa
| Temp | 60 | C | 293.4 | kJ/kg
|  | 70 | C | 303.87 | kJ/kg
|  | h 0,80 Mpa | 298.1115 | kJ/kg
Interpolasi P2 0,98 MPa :
|  | h2 = | 298.4426 | kJ/kg
T3 = 42,5 C | Temp | 42 | C | 111.28 | kJ/kg
|  | 44 | C | 114.3 | kJ/kg
|  | h3 = | 112.035 | kJ/kg
|  | h4 = | 112.035 | kJ/kg
Sesudah Mechanical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C)
| In | Out | In | Out
45% | 20.4 | 16:01 | 29.7 | 32.8 | 22.1 | 0.82 | 0.36 | 17.6 | 50.2 | 36.6
55% | 19.7 | 16.1 | 28.7 | 31.2 | 23.9 | 0.78 | 0.35 | 18 | 51.5 | 35
60% | 20 | 16 | 29.1 | 32.9 | 24.4 | 0.83 | 0.36 | 16.8 | 51.8 | 37
Load 45%
Diket | T1 = | 17.6 | (Superheated vapor) |  |  |  | h1 = | 258.671 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 286.5292 | kJ/kg
| T2 = | 50.2 | (Superheated) |  |  |  | h3 = | 103.228 | kJ/kg
| P2 = | 0.82 | Mpa |  |  |  | h4 = | 103.228 | kJ/kg
| T3 = | 36.6 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,32 Mpa | [6 empty] | Wcomp = | h2 - h1
T1 = 17,6 C | Temp | 10 | C | 259.51 | kJ/kg |  |  |  | 27.8582 | kJ/kg
P1 = 0,36 Mpa |  | 20 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h 0,32 Mpa | 260.3308 | kJ/kg |  |  |  | Qcond = | h2 - h3
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,4 Mpa | [7 empty] | 183.3012 | kJ/kg
| Temp | 10 | C | 256.59 | kJ/kg |  | c. Kalor Evaporator
|  | 20 | C | 265.88 | kJ/kg |  |  | Qevap = | h1 - h4
|  | h 0,4 Mpa | 263.6504 | kJ/kg |  |  |  |  | 155.443 | kJ/kg
| Interpolasi P1 0,36 Mpa | [5 empty] | d. COP
|  | h1 = | 258.671 | kJ/kg |  |  |  | COP = | Qevap/Wcomp
T2 = 50,2 C | [8 empty] | 5.5798
P2 = 0,82 | Tabel Superheated Refrigerant R134a 0,8 Mpa
| Temp | 50 | C | 286.71 | kJ/kg
|  | 60 | C | 296.82 | kJ/kg
|  | h 0,80 Mpa | 286.9122 | kJ/kg
Tabel Superheated Refrigerant R134a 0,9 Mpa
| Temp | 50 | C | 284.79 | kJ/kg
|  | 60 | C | 295.15 | kJ/kg
|  | h 0,90 Mpa | 284.9972 | kJ/kg
Interpolasi P2 0,82 Mpa :
|  | h2 = | 286.5292 | kJ/kg
T3 = 36,6 C | Temp | 36 | C | 102.34 | kJ/kg
|  | 38 | C | 105.3 | kJ/kg
|  | h3 = | 103.228 | kJ/kg
|  | h4 = | 103.228 | kJ/kg
Load 55%
Diket | T1 = | 18 | (Superheated vapor) |  |  |  | h1 = | 259.006 | kJ/kg
| P1 = | 0.35 | Mpa |  |  |  | h2 = | 288.5862 | kJ/kg
| T2 = | 51.5 | (Superheated) |  |  |  | h3 = | 100.875 | kJ/kg
| P2 = | 0.78 | Mpa |  |  |  | h4 = | 100.875 | kJ/kg
| T3 = | 35 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,32 Mpa | [6 empty] | Wcomp = | h2 - h1
T1 = 18 C | Temp | 10 | C | 259.51 | kJ/kg |  |  |  | 29.5802 | kJ/kg
P1 = 0,35 Mpa |  | 20 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h 0,32 Mpa | 260.374 | kJ/kg |  |  |  | Qcond = | h2 - h3
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,4 Mpa | [7 empty] | 187.7112 | kJ/kg
| Temp | 10 | C | 256.59 | kJ/kg |  | c. Kalor Evaporator
|  | 20 | C | 265.88 | kJ/kg |  |  | Qevap = | h1 - h4
|  | h 0,4 Mpa | 264.022 | kJ/kg |  |  |  |  | 158.131 | kJ/kg
| Interpolasi P1 0,35 Mpa | [5 empty] | d. COP
|  | h1 = | 259.006 | kJ/kg |  |  |  | COP = | Qevap/Wcomp
T2 = 51,5 C | [8 empty] | 5.3458
P2 = 0,78 Mpa | Menggunakan Interpolasi
Tabel Superheated Refrigerant R134a 0,70 Mpa
| Temp | 50 | C | 288.54 | kJ/kg
|  | 60 | C | 298.44 | kJ/kg
|  | h 0,70 Mpa | 290.025 | kJ/kg
Tabel Superheated Refrigerant R134a 0,80 Mpa
| Temp | 50 | C | 286.71 | kJ/kg
|  | 60 | C | 296.82 | kJ/kg
|  | h 0,80 Mpa | 288.2265 | kJ/kg
Interpolasi P2 0,78 Mpa :
|  | h2 = | 288.5862 | kJ/kg
T3 = 35 C | Temp | 34 | C | 99.41 | kJ/kg
|  | 36 | C | 102.34 | kJ/kg
|  | h3 = | 100.875 | kJ/kg
|  | h4 = | 100.875 | kJ/kg
Load 60%
Diket | T1 = | 16.8 | (Superheated vapor) |  |  |  | h1 = | 258.913 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 287.9673 | kJ/kg
| T2 = | 51.8 | (Superheated) |  |  |  | h3 = | 103.82 | kJ/kg
| P2 = | 0.83 | Mpa |  |  |  | h4 = | 103.82 | kJ/kg
| T3 = | 37 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,32 Mpa | [6 empty] | Wcomp = | h2 - h1
T1 = 16,8 C | Temp | 10 | C | 259.51 | kJ/kg |  |  |  | 29.0543 | kJ/kg
P1 = 0,36 Mpa |  | 20 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h 0,32 Mpa | 260.2444 | kJ/kg |  |  |  | Qcond = | h2 - h3
| Dengan menggunakan table A-13 Refirgerant R134a P = 0,4 Mpa | [7 empty] | 184.1473 | kJ/kg
| Temp | 10 | C | 256.59 | kJ/kg |  | c. Kalor Evaporator
|  | 20 | C | 265.88 | kJ/kg |  |  | Qevap = | h1 - h4
|  | h 0,4 Mpa | 262.9072 | kJ/kg |  |  |  |  | 155.093 | kJ/kg
| Interpolasi P1 0,36 Mpa | [5 empty] | d. COP
|  | h1 = | 258.913 | kJ/kg |  |  |  | COP = | Qevap/Wcomp
T2 = 51,8 C | [8 empty] | 5.338
P2 = 0,83 | Tabel Superheated Refrigerant R134a 0,8 Mpa
| Temp | 50 | C | 286.71 | kJ/kg
|  | 60 | C | 296.82 | kJ/kg
|  | h 0,80 Mpa | 288.5298 | kJ/kg
Tabel Superheated Refrigerant R134a 0,9 Mpa
| Temp | 50 | C | 284.79 | kJ/kg
|  | 60 | C | 295.15 | kJ/kg
|  | h 0,90 Mpa | 286.6548 | kJ/kg
Interpolasi P2 0,83 Mpa :
|  | h2 = | 287.9673 | kJ/kg
T3 = 37 C | Temp | 36 | C | 102.34 | kJ/kg
|  | 38 | C | 105.3 | kJ/kg
|  | h3 = | 103.82 | kJ/kg
|  | h4 = | 103.82 | kJ/kg
Sesudah Chemical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C)
| In | Out | In | Out
45% | 20.7 | 16.4 | 29 | 31.7 | 23.5 | 0.78 | 0.37 | 17.7 | 49.6 | 35
55% | 19.4 | 15.8 | 27.5 | 29.9 | 21.7 | 0.74 | 0.36 | 16.9 | 49.8 | 33.3
60% | 20.1 | 16 | 27.5 | 30.5 | 23.9 | 0.76 | 0.36 | 17.7 | 49.6 | 34.2
Load 45%
Diket | T1 = | 17.7 | (Superheated vapor) |  |  |  | h1 = | 260.428 | kJ/kg
| P1 = | 0.37 | Mpa |  |  |  | h2 = | 286.6684 | kJ/kg
| T2 = | 49.6 | (Superheated) |  |  |  | h3 = | 100.875 | kJ/kg
| P2 = | 0.78 | Mpa |  |  |  | h4 = | 100.875 | kJ/kg
| T3 = | 35 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 17,7 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 26.2404 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h1 = | 260.428 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,6 C | [8 empty] | 185.7934 | kJ/kg
P2 = 0,78 | Tabel Superheated Refrigerant R134a 0,7 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 40 | C | 278.59 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 288.54 | kJ/kg |  |  |  | 159.553 | kJ/kg
|  | h 0,70 Mpa | 288.142 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,8 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 40 | C | 276.46 | kJ/kg |  |  |  | 6.0804
|  | 50 | C | 286.71 | kJ/kg
|  | h 0,80 Mpa | 286.3 | kJ/kg
Interpolasi P2 0,78 Mpa :
|  | h2 = | 286.6684 | kJ/kg
T3 = 35 C | Temp | 34 | C | 99.41 | kJ/kg
|  | 36 | C | 102.34 | kJ/kg
|  | h3 = | 100.875 | kJ/kg
|  | h4 = | 100.875 | kJ/kg
Load 55%
Diket | T1 = | 16.9 | (Saturated vapor) |  |  |  | h1 = | 259.996 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 287.6066 | kJ/kg
| T2 = | 49.8 | (Superheated) |  |  |  | h3 = | 98.388 | kJ/kg
| P2 = | 0.74 | Mpa |  |  |  | h4 = | 98.388 | kJ/kg
| T3 = | 33.3 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 16,9 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 27.6106 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h1 = | 259.996 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,8 C | [8 empty] | 189.2186 | kJ/kg
P2 = 0,74 | Tabel Superheated Refrigerant R134a 0,7 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 40 | C | 278.59 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 288.54 | kJ/kg |  |  |  | 161.608 | kJ/kg
|  | h 0,70 Mpa | 288.341 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,8 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 40 | C | 276.46 | kJ/kg |  |  |  | 5.8531
|  | 50 | C | 286.71 | kJ/kg
|  | h 0,80 Mpa | 286.505 | kJ/kg
Interpolasi P2 0,74 Mpa :
|  | h2 = | 287.6066 | kJ/kg
T3 = 33,3 C | Temp | 32 | C | 96.49 | kJ/kg
|  | 34 | C | 99.41 | kJ/kg
|  | h3 = | 98.388 | kJ/kg
|  | h4 = | 98.388 | kJ/kg
Load 60%
Diket | T1 = | 17.7 | (Saturated vapor) |  |  |  | h1 = | 259.672 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 287.221 | kJ/kg
| T2 = | 49.6 | (Superheated) |  |  |  | h3 = | 98.959 | kJ/kg
| P2 = | 0.76 | Mpa |  |  |  | h4 = | 98.959 | kJ/kg
| T3 = | 34.2 | (saturated liquid)
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance
Jawab | [6 empty] | a. Kerja Kompresor
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1
T1 = 17,7 C | Temp | 16 | C | 259.51 | kJ/kg |  |  |  | 27.549 | kJ/kg
|  | 18 | C | 260.59 | kJ/kg |  | b. Kalor Kondensor
|  | h1 = | 259.672 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,6 C | [8 empty] | 188.262 | kJ/kg
P2 = 0,76 | Tabel Superheated Refrigerant R134a 0,7 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 40 | C | 278.59 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 288.54 | kJ/kg |  |  |  | 160.713 | kJ/kg
|  | h 0,70 Mpa | 288.142 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,8 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 40 | C | 276.46 | kJ/kg |  |  |  | 5.8337
|  | 50 | C | 286.71 | kJ/kg
|  | h 0,80 Mpa | 286.3 | kJ/kg
Interpolasi P2 0,75 Mpa :
|  | h2 = | 287.221 | kJ/kg
T3 = 34,2 C | Temp | 34 | C | 98.67 | kJ/kg
|  | 36 | C | 101.56 | kJ/kg
|  | h3 = | 98.959 | kJ/kg
|  | h4 = | 98.959 | kJ/kg
Kondisi | Load (%) | Enthalpy kJ/kg | [6 empty] | COP
|  | h1 | h2 | h3 | h4 | Wcomp | Qcond | Qevap
Sebelum Mechanical Cleaning | 45 | 259.672 | 293.9235 | 113.696 | 113.696 | 34.2515 | 180.2275 | 145.976 | 4.2619
| 55 | 259.672 | 293.9824 | 114.149 | 114.149 | 34.3104 | 179.8334 | 145.523 | 4.2414
| 60 | 260.374 | 298.4426 | 112.035 | 112.035 | 38.0686 | 186.4076 | 148.339 | 3.8966
Sesudah Mechanical Cleaning | 45 | 260.374 | 286.5292 | 103.228 | 103.228 | 26.1552 | 183.3012 | 157.146 | 6.0082
| 55 | 260.59 | 288.5862 | 100.875 | 100.875 | 27.9962 | 187.7112 | 159.715 | 5.7049
| 60 | 259.942 | 287.9673 | 103.82 | 103.82 | 28.0253 | 184.1473 | 156.122 | 5.5708
Sesudah Chemical Cleaning | 45 | 260.428 | 286.6684 | 100.875 | 100.875 | 26.2404 | 185.7934 | 159.553 | 6.0804
| 55 | 259.996 | 287.6066 | 98.388 | 98.388 | 27.6106 | 189.2186 | 161.608 | 5.8531
| 60 | 259.672 | 287.221 | 98.959 | 98.959 | 27.549 | 188.262 | 160.713 | 5.8337

## Perhitungan h1-h4 rev (3)
[6 empty] | p2 | p1 | t1 | t2 | t3
Sebelum Mechanical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C)
| In | Out | In | Out
45% | 18 | 14.5 | 27.7 | 30 | 25.4 | 1 | 0.34 | 16.3 | 60.5 | 43.6
55% | 18 | 14.4 | 27.3 | 29.7 | 27.4 | 1.02 | 0.34 | 16.3 | 60.2 | 43.9
60% | 17.9 | 14.8 | 28.4 | 30.6 | 28 | 0.98 | 0.34 | 17.6 | 64.5 | 42.5
Load 45% | [13 empty] | Mr = Que/Qevap
Diket | T1 = | 16.3 | (Saturated vapor) |  |  |  | h1 = | 408.1 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 442.33 | kJ/kg
| T2 = | 60.5 | (Superheated) |  |  |  | h3 = | 262.06 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 1 | Mpa |  |  |  | h4 = | 262.06 | kJ/kg
| T3 = | 43.6 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.1298 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 5647.95 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 29744.55 | kJ/s
T1 = 16,3 C | Temp | 16 | C | 407.8 | kJ/kg |  |  |  | 34.23 | kJ/kg | Qevap = | 24096.6 | kJ/s
|  | 17 | C | 408.8 | kJ/kg |  | b. Kalor Kondensor |  |  |  | COP = | 4.2664
| Menggunakan Interpolasi | [6 empty] | Qcond = | h2 - h3
[9 empty] | 180.27 | kJ/kg | PF = | 5.2664
[7 empty] | c. Kalor Evaporator |  |  |  | COP Teori = | 6.5486
[8 empty] | Qevap = | h1 - h4 |  | Eff % = | 65.15%
|  | h1 = | 408.1 | kJ/kg |  |  |  |  | 146.04 | kJ/kg
T2 = 60,5 C | [6 empty] | d. COP
P2 = 1 Mpa | Tabel Superheated Refrigerant R134a 1 MPa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 60 | C | 441.8 | kJ/kg |  |  |  | 4.2664
|  | 65 | C | 447.1 | kJ/kg
|  | h2 = | 442.33 | kJ/kg
T3 = 43,6 | Temp | 43 | C | 261.1 | kJ/kg
|  | 44 | C | 262.7 | kJ/kg
|  | h3 = | 262.06 | kJ/kg
|  | h4 = | 262.06 | kJ/kg
Load 55%
Diket | T1 = | 16.3 | (Saturated vapor) |  |  |  | h1 = | 407.98 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 442.3712 | kJ/kg
| T2 = | 60.2 | (Superheated) |  |  |  | h3 = | 262.54 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 1.02 | Mpa |  |  |  | h4 = | 262.54 | kJ/kg
| T3 = | 43.9 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.1345 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 5674.548 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 29672.148 | kJ/s
T1 = 16,3 C | Temp | 16 | C | 407.8 | kJ/kg |  |  |  | 34.3912 | kJ/kg | Qevap = | 23997.6 | kJ/s
|  | 17 | C | 408.4 | kJ/kg |  | b. Kalor Kondensor |  |  |  | COP = | 4.229
| Menggunakan Interpolasi | [6 empty] | Qcond = | h2 - h3
[9 empty] | 179.8312 | kJ/kg | PF = | 5.229
[7 empty] | c. Kalor Evaporator |  |  |  | COP Teori = | 6.5934
[8 empty] | Qevap = | h1 - h4 |  | Eff % = | 64.14%
|  | h1 = | 407.98 | kJ/kg |  |  |  |  | 145.44 | kJ/kg
T2 = 60,2 C | [6 empty] | d. COP
P2 = 1,02 Mpa | [7 empty] | COP = | Qevap/Wcomp
| Tabel Superheated Refrigerant R134a 1 MPa | [7 empty] | 4.229
| Temp | 60 | C | 441.8 | kJ/kg
|  | 65 | C | 447.1 | kJ/kg
|  | h 1 Mpa | 442.012 | kJ/kg
Tabel Superheated Refrigerant R134a 1,1 MPa
| Temp | 60 | C | 440 | kJ/kg
|  | 65 | C | 445.4 | kJ/kg
|  | h 1,1 Mpa | 440.216 | kJ/kg
Interpolasi P2 1,02 MPa :
|  | h2 = | 442.3712 | kJ/kg
T3 = 43,9 | Temp | 43 | C | 261.1 | kJ/kg
|  | 44 | C | 262.7 | kJ/kg
|  | h3 = | 262.54 | kJ/kg
|  | h4 = | 262.54 | kJ/kg
Load 60%
Diket | T1 = | 17.6 | (Saturated vapor) |  |  |  | h1 = | 408.7 | kJ/kg
| P1 = | 0.34 | Mpa |  |  |  | h2 = | 446.732 | kJ/kg
| T2 = | 64.5 | (Superheated) |  |  |  | h3 = | 260.35 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 0.98 | Mpa |  |  |  | h4 = | 260.35 | kJ/kg
| T3 = | 42.5 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.1122 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 6275.28 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 30753.03 | kJ/s
T1 = 17,6 C | Temp | 17 | C | 408.4 | kJ/kg |  |  |  | 38.032 | kJ/kg | Qevap = | 24477.75 | kJ/s
|  | 18 | C | 408.9 | kJ/kg |  | b. Kalor Kondensor |  |  |  | COP = | 3.9007
| Menggunakan Interpolasi | [6 empty] | Qcond = | h2 - h3
[9 empty] | 186.382 | kJ/kg | PF = | 4.9007
[7 empty] | c. Kalor Evaporator |  |  |  | COP Teori = | 6.1994
[8 empty] | Qevap = | h1 - h4 |  | Eff % = | 62.92%
|  | h1 = | 408.7 | kJ/kg |  |  |  |  | 148.35 | kJ/kg
T2 = 64,5 C | [6 empty] | d. COP
P2 = 0,98 Mpa | [7 empty] | COP = | Qevap/Wcomp
| Tabel Superheated Refrigerant R134a 0,95 MPa | [7 empty] | 3.9007
| Temp | 60 | C | 442.7 | kJ/kg
|  | 65 | C | 447.9 | kJ/kg
|  | h 0,95 Mpa | 447.38 | kJ/kg
Tabel Superheated Refrigerant R134a 1 MPa
| Temp | 60 | C | 441.8 | kJ/kg
|  | 65 | C | 447.1 | kJ/kg
|  | h 1 Mpa | 446.57 | kJ/kg
Interpolasi P2 0,98 MPa :
|  | h2 = | 446.732 | kJ/kg
T3 = 42,5 C | Temp | 42 | C | 259.6 | kJ/kg
|  | 43 | C | 261.1 | kJ/kg
|  | h3 = | 260.35 | kJ/kg
|  | h4 = | 260.35 | kJ/kg
Sesudah Mechanical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C)
| In | Out | In | Out
45% | 20.4 | 16:01 | 29.7 | 32.8 | 22.1 | 0.82 | 0.36 | 17.6 | 50.2 | 36.6
55% | 19.7 | 16.1 | 28.7 | 31.2 | 23.9 | 0.78 | 0.35 | 18 | 51.5 | 35
60% | 20 | 16 | 29.1 | 32.9 | 24.4 | 0.83 | 0.36 | 16.8 | 51.8 | 37
Load 45%
Diket | T1 = | 17.6 | (Saturated vapor) |  |  |  | h1 = | 408.7 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 434.9056 | kJ/kg
| T2 = | 50.2 | (Superheated) |  |  |  | h3 = | 251.5 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 0.82 | Mpa |  |  |  | h4 = | 251.5 | kJ/kg
| T3 = | 36.6 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.0496 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 4323.924 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 30261.924 | kJ/s
T1 = 17,6 C | Temp | 17 | C | 408.4 | kJ/kg |  |  |  | 26.2056 | kJ/kg | Qevap = | 25938 | kJ/s
|  | 18 | C | 408.9 | kJ/kg |  | b. Kalor Kondensor |  |  |  | COP = | 5.9987
|  | h1 = | 408.7 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 50,2 C | [8 empty] | 183.4056 | kJ/kg | PF = | 6.9987
P2 = 0,82 | Tabel Superheated Refrigerant R134a 0,8 Mpa | [5 empty] | c. Kalor Evaporator |  |  |  | COP Teori = | 8.9187
| Temp | 50 | C | 435.1 | kJ/kg |  |  | Qevap = | h1 - h4 |  | Eff % = | 67.26%
|  | 55 | C | 440.2 | kJ/kg |  |  |  | 157.2 | kJ/kg
|  | h 0,80 Mpa | 435.304 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,85 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 50 | C | 434.1 | kJ/kg |  |  |  | 5.9987
|  | 55 | C | 439.3 | kJ/kg
|  | h 0,85 Mpa | 434.308 | kJ/kg
Interpolasi P2 0,82 Mpa :
|  | h2 = | 434.9056 | kJ/kg
T3 = 36,6 C | Temp | 36 | C | 250.6 | kJ/kg
|  | 37 | C | 252.1 | kJ/kg
|  | h3 = | 251.5 | kJ/kg
|  | h4 = | 251.5 | kJ/kg
Load 55%
Diket | T1 = | 18 | (Saturated vapor) |  |  |  | h1 = | 408.9 | kJ/kg
| P1 = | 0.35 | Mpa |  |  |  | h2 = | 436.978 | kJ/kg
| T2 = | 51.5 | (Superheated) |  |  |  | h3 = | 249.2 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 0.78 | Mpa |  |  |  | h4 = | 249.2 | kJ/kg
| T3 = | 35 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.0332 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 4632.87 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 30983.37 | kJ/s
T1 = 18 C | Temp | 18 | C | 408.9 | kJ/kg |  |  |  | 28.078 | kJ/kg | Qevap = | 26350.5 | kJ/s
|  | h1 = | 408.9 | kJ/kg |  |  | b. Kalor Kondensor |  |  |  | COP = | 5.6877
T2 = 51,5 C | [7 empty] | Qcond = | h2 - h3
P2 = 0,78 Mpa | Menggunakan Interpolasi | [7 empty] | 187.778 | kJ/kg
c. Kalor Evaporator
[8 empty] | Qevap = | h1 - h4
[9 empty] | 159.7 | kJ/kg
| Tabel Superheated Refrigerant R134a 0,75 Mpa | [5 empty] | d. COP
| Temp | 50 | C | 436 | kJ/kg |  |  | COP = | Qevap/Wcomp
|  | 55 | C | 441 | kJ/kg |  |  |  | 5.6877
|  | h 0,70 Mpa | 437.5 | kJ/kg
Tabel Superheated Refrigerant R134a 0,80 Mpa
| Temp | 50 | C | 435.1 | kJ/kg
|  | 55 | C | 440.2 | kJ/kg
|  | h 0,80 Mpa | 436.63 | kJ/kg
Interpolasi P2 0,78 Mpa :
|  | h2 = | 436.978 | kJ/kg
T3 = 35 C | Temp | 35 | C | 249.2 | kJ/kg
|  | h3 = | 249.2 | kJ/kg
|  | h4 = | 249.2 | kJ/kg
Load 60%
Diket | T1 = | 16.8 | (Saturated vapor) |  |  |  | h1 = | 408.28 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 436.3576 | kJ/kg
| T2 = | 51.8 | (Superheated) |  |  |  | h3 = | 252.1 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 0.83 | Mpa |  |  |  | h4 = | 252.1 | kJ/kg
| T3 = | 37 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.0565 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 4632.804 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 30402.504 | kJ/s
T1 = 16,8 C | Temp | 16 | C | 407.8 | kJ/kg |  |  |  | 28.0776 | kJ/kg | Qevap = | 25769.7 | kJ/s
|  | 17 | C | 408.4 | kJ/kg |  | b. Kalor Kondensor |  |  |  | COP = | 5.5624
|  | h1 = | 408.28 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 51,8 C | [8 empty] | 184.2576 | kJ/kg
P2 = 0,83 | Tabel Superheated Refrigerant R134a 0,8 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 50 | C | 435.1 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 55 | C | 440.2 | kJ/kg |  |  |  | 156.18 | kJ/kg
|  | h 0,80 Mpa | 436.936 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,85 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 50 | C | 434.1 | kJ/kg |  |  |  | 5.5624
|  | 55 | C | 439.3 | kJ/kg
|  | h 0,85 Mpa | 435.972 | kJ/kg
Interpolasi P2 0,83 Mpa :
|  | h2 = | 436.3576 | kJ/kg
T3 = 37 C | Temp | 37 | C | 252.1 | kJ/kg
|  | h3 = | 252.1 | kJ/kg
|  | h4 = | 252.1 | kJ/kg
Sesudah Chemical Cleaning
Load Comp (%) | Temperatur Chilled Water (°C) |  | Temperatur Water Cond (°C) |  | Current Motor (A) | Pressure Cond (MPa) | Pressure Evap (MPa) | Temp. suction gas (°C) | Temp. delivery gas (°C) | Temp. cond saturated (°C)
| In | Out | In | Out
45% | 20.7 | 16.4 | 29 | 31.7 | 23.5 | 0.78 | 0.37 | 17.7 | 49.6 | 35
55% | 19.4 | 15.8 | 27.5 | 29.9 | 21.7 | 0.74 | 0.36 | 16.9 | 49.8 | 33.3
60% | 20.1 | 16 | 27.5 | 30.5 | 23.9 | 0.76 | 0.36 | 17.7 | 49.6 | 34.2
Load 45%
Diket | T1 = | 17.7 | (Saturated vapor) |  |  |  | h1 = | 408.75 | kJ/kg
| P1 = | 0.37 | Mpa |  |  |  | h2 = | 435.0552 | kJ/kg
| T2 = | 49.6 | (Superheated) |  |  |  | h3 = | 249.2 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 0.78 | Mpa |  |  |  | h4 = | 249.2 | kJ/kg
| T3 = | 35 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.0342 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 4340.358 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 30666.108 | kJ/s
T1 = 17,7 C | Temp | 17 | C | 408.4 | kJ/kg |  |  |  | 26.3052 | kJ/kg | Qevap = | 26325.75 | kJ/s
|  | 18 | C | 408.9 | kJ/kg |  | b. Kalor Kondensor |  |  |  | COP = | 6.0653
|  | h1 = | 408.75 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,6 C | [8 empty] | 185.8552 | kJ/kg
P2 = 0,78 | Tabel Superheated Refrigerant R134a 0,75 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 45 | C | 431 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 436 | kJ/kg |  |  |  | 159.55 | kJ/kg
|  | h 0,70 Mpa | 435.6 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,8 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 45 | C | 430 | kJ/kg |  |  |  | 6.0653
|  | 50 | C | 435.1 | kJ/kg
|  | h 0,80 Mpa | 434.692 | kJ/kg
Interpolasi P2 0,78 Mpa :
|  | h2 = | 435.0552 | kJ/kg
T3 = 35 C | Temp | 35 | C | 249.2 | kJ/kg
|  | h3 = | 249.2 | kJ/kg
|  | h4 = | 249.2 | kJ/kg
Load 55%
Diket | T1 = | 16.9 | (Saturated vapor) |  |  |  | h1 = | 408.34 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 436 | kJ/kg
| T2 = | 49.8 | (Superheated) |  |  |  | h3 = | 246.65 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 0.74 | Mpa |  |  |  | h4 = | 246.65 | kJ/kg
| T3 = | 33.3 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.0205 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 4563.9 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 31242.75 | kJ/s
T1 = 16,9 C | Temp | 16 | C | 407.8 | kJ/kg |  |  |  | 27.66 | kJ/kg | Qevap = | 26678.85 | kJ/s
|  | 17 | C | 408.4 | kJ/kg |  | b. Kalor Kondensor |  |  |  | COP = | 5.8456
|  | h1 = | 408.34 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,8 C | [8 empty] | 189.35 | kJ/kg
P2 = 0,74 | Tabel Superheated Refrigerant R134a 0,725 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 45 | C | 431.5 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 436.5 | kJ/kg |  |  |  | 161.69 | kJ/kg
|  | h 0,70 Mpa | 436.3 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,75 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 45 | C | 431 | kJ/kg |  |  |  | 5.8456
|  | 50 | C | 436 | kJ/kg
|  | h 0,75 Mpa | 435.8 | kJ/kg
Interpolasi P2 0,74 Mpa :
|  | h2 = | 436 | kJ/kg
T3 = 33,3 C | Temp | 33 | C | 246.2 | kJ/kg
|  | 34 | C | 247.7 | kJ/kg
|  | h3 = | 246.65 | kJ/kg
|  | h4 = | 246.65 | kJ/kg
Load 60%
Diket | T1 = | 17.7 | (Saturated vapor) |  |  |  | h1 = | 408.05 | kJ/kg
| P1 = | 0.36 | Mpa |  |  |  | h2 = | 435.4184 | kJ/kg
| T2 = | 49.6 | (Superheated) |  |  |  | h3 = | 248 | kJ/kg |  | Menggunakan Laju Aliran Massa
| P2 = | 0.76 | Mpa |  |  |  | h4 = | 248 | kJ/kg
| T3 = | 34.2 | (saturated liquid) | [7 empty] | Que = | 165 | kW
Ditanya | h1, h2, h3, h4 | [5 empty] | Performance |  |  |  | Mr = | 1.0309 | Kg/s
Jawab | [6 empty] | a. Kerja Kompresor |  |  |  | Wcomp = | 4515.786 | kW
| Dengan menggunakan table A-13 Refirgerant R134a | [6 empty] | Wcomp = | h2 - h1 |  | Qcond = | 30924.036 | kJ/s
T1 = 17,7 C | Temp | 17 | C | 408.4 | kJ/kg |  |  |  | 27.3684 | kJ/kg | Qevap = | 26408.25 | kJ/s
|  | 18 | C | 408.9 | kJ/kg |  | b. Kalor Kondensor |  |  |  | COP = | 5.848
|  | h1 = | 408.05 | kJ/kg |  |  |  | Qcond = | h2 - h3
T2 = 49,6 C | [8 empty] | 187.4184 | kJ/kg
P2 = 0,76 | Tabel Superheated Refrigerant R134a 0,75 Mpa | [5 empty] | c. Kalor Evaporator
| Temp | 45 | C | 431 | kJ/kg |  |  | Qevap = | h1 - h4
|  | 50 | C | 436 | kJ/kg |  |  |  | 160.05 | kJ/kg
|  | h 0,75 Mpa | 435.6 | kJ/kg |  |  | d. COP
| Tabel Superheated Refrigerant R134a 0,8 Mpa | [6 empty] | COP = | Qevap/Wcomp
| Temp | 45 | C | 430 | kJ/kg |  |  |  | 5.848
|  | 50 | C | 435.1 | kJ/kg
|  | h 0,80 Mpa | 434.692 | kJ/kg
Interpolasi P2 0,75 Mpa :
|  | h2 = | 435.4184 | kJ/kg
T3 = 34,2 C | Temp | 34 | C | 247.7 | kJ/kg
|  | 35 | C | 249.2 | kJ/kg
|  | h3 = | 248 | kJ/kg
|  | h4 = | 248 | kJ/kg
Kondisi | Load (%) | Enthalpy kJ/kg | [6 empty] | COP
|  | h1 | h2 | h3 | h4 | Wcomp | Qcond | Qevap
Sebelum Mechanical Cleaning | 45 | 408.1 | 442.33 | 262.06 | 262.06 | 34.23 | 180.27 | 146.04 | 4.2664
| 55 | 407.98 | 442.3712 | 262.54 | 262.54 | 34.3912 | 179.8312 | 145.44 | 4.229
| 60 | 408.7 | 446.732 | 260.35 | 260.35 | 38.032 | 186.382 | 148.35 | 3.9007
Sesudah Mechanical Cleaning | 45 | 408.7 | 434.9056 | 251.5 | 251.5 | 26.2056 | 183.4056 | 157.2 | 5.9987
| 55 | 408.9 | 436.978 | 249.2 | 249.2 | 28.078 | 187.778 | 159.7 | 5.6877
| 60 | 408.28 | 436.3576 | 252.1 | 252.1 | 28.0776 | 184.2576 | 156.18 | 5.5624
Sesudah Chemical Cleaning | 45 | 408.75 | 435.0552 | 249.2 | 249.2 | 26.3052 | 185.8552 | 159.55 | 6.0653
| 55 | 408.34 | 436 | 246.65 | 246.65 | 27.66 | 189.35 | 161.69 | 5.8456
| 60 | 408.05 | 435.4184 | 248 | 248 | 27.3684 | 187.4184 | 160.05 | 5.848
𝑀𝑟=𝑄_𝑢𝑒/(ℎ_1− ℎ_4 )
𝑊_𝑐𝑜𝑚𝑝= ℎ_2−ℎ_1
𝑄_𝑒𝑣𝑎𝑝=𝑀𝑟 (ℎ_1−ℎ_4)
𝑄_𝑐𝑜𝑛𝑑=𝑀𝑟 (ℎ_2−ℎ_3)
𝐶𝑂𝑃=𝑄_𝑒𝑣𝑎𝑝/𝑊_𝑐𝑜𝑚𝑝
PF=𝑄_𝑐𝑜𝑛𝑑/𝑊_𝑐𝑜𝑚𝑝
Mr = Laju Aliran (Kg/s)
Wcomp = Kerja Kompresor (kW)
Qevap = Daya Evaporator (Kj/s)
Qcond = Daya Kondensor (Kj/s)
COP = Coefficient Of Performance
PF = Performance Factor
〖𝐶𝑂𝑃〗_𝑡𝑒𝑜𝑟𝑖𝑡𝑖𝑠=(〖𝑇𝑒𝑚𝑝〗_𝑒𝑣𝑎𝑝+273,15 𝐾)/(〖𝑇𝑒𝑚𝑝〗_𝑐𝑜𝑛𝑑−〖𝑇𝑒𝑚𝑝〗_𝐸𝑣𝑎𝑝 )
Effisiensi=〖𝐶𝑂𝑃〗_𝑎𝑐𝑡/〖𝐶𝑂𝑃〗_𝑡𝑒𝑜𝑟𝑖

## Load 45
Sebelum Mechanical Cleaning
Sesudah Mechanical Cleaning
Sesudah Chemical Cleaning

## Load 55
Sebelum Mechanical Cleaning
Sesudah Mechanical Cleaning
Sesudah Chemical Cleaning

## Load 60
Sebelum Mechanical Cleaning
Sesudah Mechanical Cleaning
Sesudah Chemical Cleaning

## Load 45 (2)
Sebelum Mechanical Cleaning
Sesudah Mechanical Cleaning
Sesudah Chemical Cleaning

## Load 55 (2)
Sebelum Mechanical Cleaning
Sesudah Mechanical Cleaning
Sesudah Chemical Cleaning

## Load 60 (2)
Sebelum Mechanical Cleaning
Sesudah Mechanical Cleaning
Sesudah Chemical Cleaning