## data produksi
Rincian Data Suhu Chiller | [7 empty] | Data Jam Kerja dan Suhu |  |  |  | Data Machine Break |  |  |  | Expert : | Teknisi outsourcing | 2
No. | Tanggal | Chiller 1 | Chiller 2 | No. | Tanggal | Chiller 1 | Chiller 2 | Mesin | Jumlah Jam Kerja (Hari) | Suhu Yang Tidak Tercapai |  | Chiller 1 |  |  |  |  | kepala teknisi | 1
1 | 2023-09-01 | 7.0 | 7.0 | 31 | 2023-10-01 | 7.2 | 7.3 | Chiller 1 | 60 | 9 |  | Tanggal | Jam | Masalah | Machine Break (Jam) |  | manajer | 1
2 | 2023-09-02 | 7.2 | 7.0 | 32 | 2023-10-02 | 7.0 | 7.1 | Chiller 2 | 60 | 8 |  | 2023-09-17 | 14:34 | COMPR STOP - Condenser Pressure High | 3
3 | 2023-09-03 | 6.5 | 6.9 | 33 | 2023-10-03 | 7.4 | 7.5 |  |  |  |  | 2023-09-18 | 18:06 | COMPR STOP - Condenser Pressure High | 1
4 | 2023-09-04 | 6.7 | 7.2 | 34 | 2023-10-04 | 7.8 | 8.0 | Tabel Loading Time |  |  |  | 2023-09-24 | 22:09 | COMPR STOP - Oil Feed Temp High | 0.4
5 | 2023-09-05 | 7.0 | 7.5 | 35 | 2023-10-05 | 8.0 | 8.5 | Mesin | Waktu Operasi Setiap Hari (Jam) | Lama Beroperasi (Hari) | Total loading time (jam) | 2023-10-09 | 13:08 | COMPR STOP - Oil Feed Temp High | 0.3
6 | 2023-09-06 | 7.3 | 7.7 | 36 | 2023-10-06 | 8.2 | 8.6 | Chiller 1 | 14 | 60 | 840 | 2023-10-13 | 15:09 | COMPR STOP - Condenser Pressure High | 2
7 | 2023-09-07 | 7.5 | 7.6 | 37 | 2023-10-07 | 8.5 | 8.5 | Chiller 2 | 14 | 60 | 840 | 2023-10-15 | 18:46 | COMPR STOP - Condenser Pressure High | 1
8 | 2023-09-08 | 7.7 | 7.8 | 38 | 2023-10-08 | 8.0 | 8.6 |  |  |  |  | 2023-10-16 | 19:23 | COMPR STOP - Oil Feed Temp High | 0.5
9 | 2023-09-09 | 8.0 | 8.3 | 39 | 2023-10-09 | 8.6 | 8.8 |  |  |  |  | 2023-10-21 | 21:10 | COMPR STOP - Evaporator Water Flow Loss | 0.5
10 | 2023-09-10 | 8.1 | 8.1 | 40 | 2023-10-10 | 7.9 | 8.7 |  |  |  |  | 2023-10-23 | 23:50 | COMPR STOP - Evaporator Water Flow Loss | 0.45
11 | 2023-09-11 | 7.8 | 8.0 | 41 | 2023-10-11 | 7.7 | 8.6 | [6 empty] | Total | 9.15
12 | 2023-09-12 | 7.7 | 8.4 | 42 | 2023-10-12 | 8.0 | 8.4 |  |  |  |  | Chiller 2
13 | 2023-09-13 | 8.1 | 8.6 | 43 | 2023-10-13 | 8.7 | 8.0 |  |  |  |  | 2023-09-13 | 13:56 | COMPR STOP - No Starter Transition | 1
14 | 2023-09-14 | 8.0 | 8.8 | 44 | 2023-10-14 | 8.5 | 8.2 |  |  |  |  | 2023-09-14 | 18:45 | NO START - Starter fault | 0.3
15 | 2023-09-15 | 8.2 | 8.2 | 45 | 2023-10-15 | 8.6 | 8.0 |  |  |  |  | 2023-09-24 | 15:12 | COMPR STOP - Evaporator Water Flow Loss | 1
16 | 2023-09-16 | 8.5 | 8.0 | 46 | 2023-10-16 | 8.8 | 7.7 |  |  |  |  | 2023-10-06 | 20:34 | COMPR STOP - Condenser Pressure High | 2
17 | 2023-09-17 | 8.7 | 7.9 | 47 | 2023-10-17 | 8.5 | 7.5 |  |  |  |  | 2023-10-09 | 21:45 | COMPR STOP - No Starter Transition | 2.5
18 | 2023-09-18 | 8.7 | 7.7 | 48 | 2023-10-18 | 8.2 | 7.3 |  |  |  |  | 2023-10-10 | 17:01 | COMPR STOP - Evaporator Water Flow Loss | 0.5
19 | 2023-09-19 | 8.5 | 7.5 | 49 | 2023-10-19 | 8.0 | 7.2 |  |  |  |  | 2023-10-11 | 22:07 | COMPR STOP - No Starter Transition | 1
20 | 2023-09-20 | 8.3 | 7.8 | 50 | 2023-10-20 | 7.7 | 7.0 |  |  |  |  | 2023-10-28 | 14:09 | NO START - Starter fault | 0.3
21 | 2023-09-21 | 8.0 | 7.5 | 51 | 2023-10-21 | 8.7 | 6.7 | [6 empty] | Total | 8.6
22 | 2023-09-22 | 7.8 | 7.6 | 52 | 2023-10-22 | 8.5 | 6.5
23 | 2023-09-23 | 8.1 | 8.0 | 53 | 2023-10-23 | 8.6 | 6.6
24 | 2023-09-24 | 8.6 | 8.8 | 54 | 2023-10-24 | 8.3 | 6.8
25 | 2023-09-25 | 8.4 | 8.4 | 55 | 2023-10-25 | 7.9 | 7.0
26 | 2023-09-26 | 8.0 | 8.2 | 56 | 2023-10-26 | 7.7 | 7.1
27 | 2023-09-27 | 7.5 | 8.0 | 57 | 2023-10-27 | 7.2 | 8.1
28 | 2023-09-28 | 7.3 | 7.7 | 58 | 2023-10-28 | 7.0 | 8.6
29 | 2023-09-29 | 7.2 | 7.5 | 59 | 2023-10-29 | 6.8 | 8.4
30 | 2023-09-30 | 7.0 | 7.3 | 60 | 2023-10-30 | 6.9 | 8.3
|  |  |  | Total jam kerja chiller dalam satuan hari |  | 60 | 60
|  |  |  | Total suhu yang tidak tercapai |  | 9 | 8

## OEE
Data jam kerja dan Delay mesin chiller
Jadwal kerja mesin chiller | Waktu yang dibutuhkan/hari (jam) | Lama beroperasi (hari) | Total waktu yang dibutuhkan (jam)
Jam kerja tersedia | 14 | 60 | 840
Warm up time | 0.33 | 60 | 19.8
Penyetelan sparepart | 0.5 | 60 | 30
Perhitungan downtime mesin chiller
Mesin | Warm up time (Jam) | Machine break (Jam) | Total downtime (Jam)
Chiller 1 | 19.8 | 9.15 | 28.95
Chiller 2 | 19.8 | 8.6 | 28.4
Perhitungan Availability mesin chiller
Mesin | Loading time (Jam) | Total downtime (Jam) | Operation time (Jam) | Availability (%)
Chiller 1 | 840 | 28.95 | 811.05 | 96.5536
Chiller 2 | 840 | 28.4 | 811.6 | 96.619
Perhitungan Total Delay
Mesin | Total downtime (Jam) | Penyetelan sparepart (Jam) | Total delay (Jam)
Chiller 1 | 28.95 | 30 | 58.95
Chiller 2 | 28.4 | 30 | 58.4
Perhitungan presentase jam kerja
Mesin | Available time (Jam) | Total delay (Jam) | Jam kerja (%)
Chiller 1 | 840 | 58.95 | 92.9821
Chiller 2 | 840 | 58.4 | 93.0476
Perhitungan Ideal cycle time
Mesin | Lama beroperasi (Hari) | Loading time (Jam) | Waktu siklus (Jam/Pcs) | Jam kerja (%) | Ideal cycle time (Jam/Pcs)
Chiller 1 | 60 | 840 | 14 | 92.9821 | 13.0175
Chiller 2 | 60 | 840 | 14 | 93.0476 | 13.0267
Perhitungan performance efficiency mesin chiller
Mesin | Lama beroperasi (Hari) | Ideal cycle time (Jam/Pcs) | Operation time (Jam) | Performance efficiency (%)
Chiller 1 | 60 | 13.0175 | 811.05 | 96.3011
Chiller 2 | 60 | 13.0267 | 811.6 | 96.3036
Perhitungan Rate of quality product mesin chiller
Mesin | Lama beroperasi (Hari) | Suhu tidak tercapai | Rate of quality (%)
Chiller 1 | 60 | 9 | 85
Chiller 2 | 60 | 8 | 86.6667
Perhitungan Overall Equipment Effectiveness
Mesin | Availibility Ratio (%) | Performance Efficiency (%) | Rate of Quality (%) | OEE (%)
Chiller 1 | 96.5536 | 96.3011 | 85 | 79.0348
Chiller 2 | 96.619 | 96.3036 | 86.6667 | 80.6413

## FMEA
|  | Teknisi |  |  | Teknisi |  |  | Kep. Tek |  |  | Manajer |  |  | Akumulasi
Failure | Failure Mode | S | O | D | S | O | D | S | O | D | S | O | D | S | O | D | RPN | Rank
Kondensor | Tekanan kondensor tinggi | 3 | 8 | 1 | 6 | 7 | 9 | 2 | 2 | 3 | 2 | 1 | 4 | 3.25 | 4.5 | 4.25 | 62.1562 | 2
Evaporator | Water loss di evaporator | 4 | 2 | 2 | 3 | 1 | 2 | 9 | 2 | 1 | 2 | 2 | 2 | 4.5 | 1.75 | 1.75 | 13.7812 | 8
Cooling Tower | Sirkulasi air tidak lancar | 3 | 1 | 1 | 6 | 2 | 2 | 1 | 2 | 3 | 8 | 1 | 1 | 4.5 | 1.5 | 1.75 | 11.8125 | 9
Kompresor | Kompressor tidak bisa menyala/tidak bisa jalan | 6 | 4 | 5 | 6 | 4 | 2 | 7 | 3 | 1 | 7 | 2 | 3 | 6.5 | 3.25 | 2.75 | 58.0938 | 3
| Kompresor berhenti mendadak | 7 | 8 | 3 | 8 | 2 | 1 | 8 | 1 | 1 | 9 | 7 | 1 | 8 | 4.5 | 1.5 | 54 | 4
| Suhu oli over high | 6 | 3 | 3 | 6 | 2 | 1 | 6 | 6 | 2 | 7 | 4 | 2 | 6.25 | 3.75 | 2 | 46.875 | 5
| Penggantian Freon | 4 | 1 | 1 | 6 | 4 | 8 | 5 | 1 | 1 | 2 | 7 | 2 | 4.25 | 3.25 | 3 | 41.4375 | 7
| Suhu kompresor overhaul | 8 | 2 | 6 | 8 | 2 | 6 | 8 | 5 | 1 | 7 | 4 | 4 | 7.75 | 3.25 | 4.25 | 107.0469 | 1
| Kurangnya oli | 4 | 8 | 6 | 4 | 7 | 1 | 2 | 2 | 2 | 5 | 1 | 1 | 3.75 | 4.5 | 2.5 | 42.1875 | 6
| Failure Mode | Teknisi S: RPN
| Tekanan kondensor tinggi | Teknisi S: 62.1562
| Water loss di evaporator | Teknisi S: 13.7812
| Sirkulasi air tidak lancar | Teknisi S: 11.8125
| Kompressor tidak bisa menyala/tidak bisa jalan | Teknisi S: 58.0938
| Kompresor berhenti mendadak | Teknisi S: 54
| Suhu oli over high | Teknisi S: 46.875
| Penggantian Freon | Teknisi S: 41.4375
| Suhu kompresor overhaul | Teknisi S: 107.0469
| Kurangnya oli | Teknisi S: 42.1875