## Equipment Description
SYSTEM NAME: GAS TURBINE GENERATOR
SPECIFICATION:
DOCUMENTATION:
DESCRIPTION:
Sistem Gas Turbine Generator merupakan sistem pembangkit tenaga listrik yang berfungsi untuk mengubah energi dari bahan bakar (gas) menjadi energi mekanik, dan selanjutnya dikonversi menjadi energi listrik melalui generator. Sistem ini dirancang untuk menghasilkan daya listrik sebesar 3800 kW dengan tegangan 6600 V dan frekuensi 50 Hz. Sistem ini digunakan dalam instalasi pembangkit industri dengan efisiensi termal sekitar 29,3% dan kapasitas output sebesar 4600 kWe. Adapun peralatan yang termasuk dalam sistem ini antara lain:
- | Air Inlet
- | Compressor
- | Combustion
- | Power Turbine
- | Transmission
- | Electric Generator
- | Fuel System
- | Starting System
- | Control & Monitoring System
- | Lubrication System
- | Cooling System
- | Fire & Gas Protection System
Exhaust System

## Function
EQUIPMENT FUNCTION - GAS TURBINE GENERATOR
NO. | EQUIPMENT | FUNCTION
1 | Air Inlet | Menyaring dan mengarahkan udara ke kompresor, memastikan udara bebas dari partikel berbahaya.
2 | Compressor | Mengompresi udara untuk pembakaran agar mencapai tekanan yang dibutuhkan.
3 | Combustion | Mencampur udara bertekanan dan bahan bakar, lalu membakarnya untuk menghasilkan energi termal.
4 | Power Turbine | Mengubah energi termal dari pembakaran menjadi energi mekanik putaran shaft.
5 | Transmission | Mentransfer putaran dari turbin ke generator secara efisien, termasuk kopling atau gearbox.
6 | Electric Generator | Mengubah energi mekanik menjadi energi listrik; menghasilkan 3800 kW pada 6600 V.
7 | Fuel System | Menyuplai bahan bakar (gas) dari sumber ke ruang bakar secara aman dan terkontrol.
8 | Starting System | Memungkinkan turbin untuk mencapai kecepatan minimum agar pembakaran bisa berlangsung (self-sustaining combustion).
9 | Control & Monitoring System | Mengendalikan operasi sistem dan memantau parameter seperti suhu, tekanan, kecepatan, dan getaran.
10 | Lubrication System | Melumasi komponen berputar untuk mengurangi gesekan dan panas serta mencegah keausan.
11 | Cooling System | Menjaga suhu sistem tetap stabil dan aman selama operasi, terutama untuk bearing dan oil cooler.
12 | Fire & Gas Protection System | Mendeteksi dan merespons kebakaran atau kebocoran gas; melindungi sistem dan personel.
13 | Exhaust System | Membuang gas hasil pembakaran ke atmosfer dan meredam suara.

## Information Sheet
INFORMATION SHEET - GAS TURBINE GENERATOR
NO | SYSTEM/EQUIPMENT | FAILURE MODE | FAILURE EFFECT | CAUSE | EVIDENT FAILURE | SAFETY IMPACT | ENVIRONMENTAL IMPACT | OPERATIONAL IMPACT | NON-OPERATIONAL IMPACT | SEVERITY (S) | OCCURRENCE (O) | DETECTION (D) | RPN
1 | Air Inlet | Abnormal instrument reading | Data monitoring tidak akurat, menyebabkan keputusan operasional salah. | Sensor kotor, kalibrasi salah, gangguan sinyal. | No | Low | None | Medium | Low | 2 | 3 | 2 | 12
| Air Inlet | Performance degradation | Efisiensi menurun, energi lebih besar dibutuhkan, output menurun. | Kotoran, aus, pendinginan tidak cukup, pelumasan menurun. | No | Low | Low | Medium | Low | 3 | 3 | 3 | 27
2 | Compressor | Breakdown | Peralatan berhenti beroperasi, bisa menyebabkan trip sistem. | Kerusakan mekanik, keausan, korosi, pelumasan tidak cukup. | Yes | High | Medium | High | Medium | 5 | 4 | 3 | 60
| Compressor | Excessive vibration | Mempercepat kerusakan mekanik, risiko kegagalan total meningkat. | Imbalance, misalignment, bearing aus atau rusak. | No | Medium | None | High | Low | 3 | 3 | 2 | 18
| Compressor | Failure to operate | Peralatan tidak bisa dinyalakan atau beroperasi saat dibutuhkan. | Motor gagal, sistem starting bermasalah, pelumas tidak cukup. | Yes | Medium | Low | High | Medium | 4 | 3 | 3 | 36
3 | Combustion | Breakdown | Peralatan berhenti beroperasi, bisa menyebabkan trip sistem. | Kerusakan mekanik, keausan, korosi, pelumasan tidak cukup. | Yes | High | Medium | High | Medium | 5 | 4 | 3 | 60
| Combustion | Failure to operate | Peralatan tidak bisa dinyalakan atau beroperasi saat dibutuhkan. | Motor gagal, sistem starting bermasalah, pelumas tidak cukup. | Yes | Medium | Low | High | Medium | 4 | 3 | 3 | 36
| Combustion | Performance degradation | Efisiensi menurun, energi lebih besar dibutuhkan, output menurun. | Kotoran, aus, pendinginan tidak cukup, pelumasan menurun. | No | Low | Low | Medium | Low | 3 | 3 | 3 | 27
4 | Power Turbine | Breakdown | Peralatan berhenti beroperasi, bisa menyebabkan trip sistem. | Kerusakan mekanik, keausan, korosi, pelumasan tidak cukup. | Yes | High | Medium | High | Medium | 5 | 4 | 3 | 60
| Power Turbine | Excessive vibration | Mempercepat kerusakan mekanik, risiko kegagalan total meningkat. | Imbalance, misalignment, bearing aus atau rusak. | No | Medium | None | High | Low | 3 | 3 | 2 | 18
| Power Turbine | Performance degradation | Efisiensi menurun, energi lebih besar dibutuhkan, output menurun. | Kotoran, aus, pendinginan tidak cukup, pelumasan menurun. | No | Low | Low | Medium | Low | 3 | 3 | 3 | 27
5 | Transmission | Breakdown | Peralatan berhenti beroperasi, bisa menyebabkan trip sistem. | Kerusakan mekanik, keausan, korosi, pelumasan tidak cukup. | Yes | High | Medium | High | Medium | 5 | 4 | 3 | 60
| Transmission | Failure to operate | Peralatan tidak bisa dinyalakan atau beroperasi saat dibutuhkan. | Motor gagal, sistem starting bermasalah, pelumas tidak cukup. | Yes | Medium | Low | High | Medium | 4 | 3 | 3 | 36
6 | Electric Generator | Power failure | Generator tidak menghasilkan listrik, gangguan pada distribusi daya. | Kerusakan winding, sistem pendingin gagal, overheat. | Yes | High | None | High | Medium | 5 | 2 | 3 | 30
| Electric Generator | Breakdown | Peralatan berhenti beroperasi, bisa menyebabkan trip sistem. | Kerusakan mekanik, keausan, korosi, pelumasan tidak cukup. | Yes | High | Medium | High | Medium | 5 | 4 | 3 | 60
| Electric Generator | Excessive vibration | Mempercepat kerusakan mekanik, risiko kegagalan total meningkat. | Imbalance, misalignment, bearing aus atau rusak. | No | Medium | None | High | Low | 3 | 3 | 2 | 18
7 | Fuel System | Failure to operate | Peralatan tidak bisa dinyalakan atau beroperasi saat dibutuhkan. | Motor gagal, sistem starting bermasalah, pelumas tidak cukup. | Yes | Medium | Low | High | Medium | 4 | 3 | 3 | 36
| Fuel System | Performance degradation | Efisiensi menurun, energi lebih besar dibutuhkan, output menurun. | Kotoran, aus, pendinginan tidak cukup, pelumasan menurun. | No | Low | Low | Medium | Low | 3 | 3 | 3 | 27
| Fuel System | Breakdown | Peralatan berhenti beroperasi, bisa menyebabkan trip sistem. | Kerusakan mekanik, keausan, korosi, pelumasan tidak cukup. | Yes | High | Medium | High | Medium | 5 | 4 | 3 | 60
8 | Starting System | Failure to operate | Peralatan tidak bisa dinyalakan atau beroperasi saat dibutuhkan. | Motor gagal, sistem starting bermasalah, pelumas tidak cukup. | Yes | Medium | Low | High | Medium | 4 | 3 | 3 | 36
| Starting System | No output | Peralatan tidak menghasilkan energi, tekanan, atau aliran. | Sistem tidak aktif, kerusakan komponen internal. | Yes | Medium | None | High | Medium | 4 | 2 | 3 | 24
9 | Control & Monitoring System | Abnormal instrument reading | Data monitoring tidak akurat, menyebabkan keputusan operasional salah. | Sensor kotor, kalibrasi salah, gangguan sinyal. | No | Low | None | Medium | Low | 2 | 3 | 2 | 12
| Control & Monitoring System | Control/ signal failure | Sistem tidak merespon perintah kontrol atau alarm tidak aktif. | Kabel sinyal rusak, PLC gagal, gangguan perangkat lunak. | No | High | Low | High | Low | 4 | 3 | 3 | 36
10 | Lubrication System | Failure to operate | Peralatan tidak bisa dinyalakan atau beroperasi saat dibutuhkan. | Motor gagal, sistem starting bermasalah, pelumas tidak cukup. | Yes | Medium | Low | High | Medium | 4 | 3 | 3 | 36
| Lubrication System | Performance degradation | Efisiensi menurun, energi lebih besar dibutuhkan, output menurun. | Kotoran, aus, pendinginan tidak cukup, pelumasan menurun. | No | Low | Low | Medium | Low | 3 | 3 | 3 | 27
| Lubrication System | Breakdown | Peralatan berhenti beroperasi, bisa menyebabkan trip sistem. | Kerusakan mekanik, keausan, korosi, pelumasan tidak cukup. | Yes | High | Medium | High | Medium | 5 | 4 | 3 | 60
11 | Cooling System | Failure to operate | Peralatan tidak bisa dinyalakan atau beroperasi saat dibutuhkan. | Motor gagal, sistem starting bermasalah, pelumas tidak cukup. | Yes | Medium | Low | High | Medium | 4 | 3 | 3 | 36
| Cooling System | Performance degradation | Efisiensi menurun, energi lebih besar dibutuhkan, output menurun. | Kotoran, aus, pendinginan tidak cukup, pelumasan menurun. | No | Low | Low | Medium | Low | 3 | 3 | 3 | 27
12 | Fire & Gas Protection System | Control/ signal failure | Sistem tidak merespon perintah kontrol atau alarm tidak aktif. | Kabel sinyal rusak, PLC gagal, gangguan perangkat lunak. | No | High | Low | High | Low | 4 | 3 | 3 | 36
| Fire & Gas Protection System | No output | Peralatan tidak menghasilkan energi, tekanan, atau aliran. | Sistem tidak aktif, kerusakan komponen internal. | Yes | Medium | None | High | Medium | 4 | 2 | 3 | 24
| Fire & Gas Protection System | Abnormal instrument reading | Data monitoring tidak akurat, menyebabkan keputusan operasional salah. | Sensor kotor, kalibrasi salah, gangguan sinyal. | No | Low | None | Medium | Low | 2 | 3 | 2 | 12
13 | Exhaust System | Failure to operate | Peralatan tidak bisa dinyalakan atau beroperasi saat dibutuhkan. | Motor gagal, sistem starting bermasalah, pelumas tidak cukup. | Yes | Medium | Low | High | Medium | 4 | 3 | 3 | 36
| Exhaust System | Performance degradation | Efisiensi menurun, energi lebih besar dibutuhkan, output menurun. | Kotoran, aus, pendinginan tidak cukup, pelumasan menurun. | No | Low | Low | Medium | Low | 3 | 3 | 3 | 27

## Summary RPN
SUMMARY RPN - GAS TURBINE GENERATOR
SYSTEM/EQUIPMENT | FAILURE MODE | SEVERITY (S) | OCCURRENCE (O) | DETECTION (D) | RPN | CUMMULATIVE RPN | CUMMULATIVE % RPN | FOLLOW UP ACTION
Compressor | Breakdown | 5 | 4 | 3 | 60 | 60 | 5.277% | RCM
Combustion | Breakdown | 5 | 4 | 3 | 60 | 120 | 10.55% | RCM
Power Turbine | Breakdown | 5 | 4 | 3 | 60 | 180 | 15.83% | RCM
Transmission | Breakdown | 5 | 4 | 3 | 60 | 240 | 21.11% | RCM
Electric Generator | Breakdown | 5 | 4 | 3 | 60 | 300 | 26.39% | SIMPLE FMEA
Fuel System | Breakdown | 5 | 4 | 3 | 60 | 360 | 31.66% | SIMPLE FMEA
Lubrication System | Breakdown | 5 | 4 | 3 | 60 | 420 | 36.94% | SIMPLE FMEA
Compressor | Failure to operate | 4 | 3 | 3 | 36 | 456 | 40.11% | SIMPLE FMEA
Combustion | Failure to operate | 4 | 3 | 3 | 36 | 492 | 43.27% | SIMPLE FMEA
Transmission | Failure to operate | 4 | 3 | 3 | 36 | 528 | 46.44% | SIMPLE FMEA
Fuel System | Failure to operate | 4 | 3 | 3 | 36 | 564 | 49.6% | SIMPLE FMEA
Starting System | Failure to operate | 4 | 3 | 3 | 36 | 600 | 52.77% | SIMPLE FMEA
Control & Monitoring System | Control/ signal failure | 4 | 3 | 3 | 36 | 636 | 55.94% | SIMPLE FMEA
Lubrication System | Failure to operate | 4 | 3 | 3 | 36 | 672 | 59.1% | SIMPLE FMEA
Cooling System | Failure to operate | 4 | 3 | 3 | 36 | 708 | 62.27% | SIMPLE FMEA
Fire & Gas Protection System | Control/ signal failure | 4 | 3 | 3 | 36 | 744 | 65.44% | SIMPLE FMEA
Exhaust System | Failure to operate | 4 | 3 | 3 | 36 | 780 | 68.6% | SIMPLE FMEA
Electric Generator | Power failure | 5 | 2 | 3 | 30 | 810 | 71.24% | SIMPLE FMEA
Air Inlet | Performance degradation | 3 | 3 | 3 | 27 | 837 | 73.61% | SIMPLE FMEA
Combustion | Performance degradation | 3 | 3 | 3 | 27 | 864 | 75.99% | SIMPLE FMEA
Power Turbine | Performance degradation | 3 | 3 | 3 | 27 | 891 | 78.36% | SIMPLE FMEA
Fuel System | Performance degradation | 3 | 3 | 3 | 27 | 918 | 80.74% | SIMPLE FMEA
Lubrication System | Performance degradation | 3 | 3 | 3 | 27 | 945 | 83.11% | NO SCHEDULED MAINTENANCE
Cooling System | Performance degradation | 3 | 3 | 3 | 27 | 972 | 85.49% | NO SCHEDULED MAINTENANCE
Exhaust System | Performance degradation | 3 | 3 | 3 | 27 | 999 | 87.86% | NO SCHEDULED MAINTENANCE
Starting System | No output | 4 | 2 | 3 | 24 | 1023 | 89.97% | NO SCHEDULED MAINTENANCE
Fire & Gas Protection System | No output | 4 | 2 | 3 | 24 | 1047 | 92.08% | NO SCHEDULED MAINTENANCE
Compressor | Excessive vibration | 3 | 3 | 2 | 18 | 1065 | 93.67% | NO SCHEDULED MAINTENANCE
Power Turbine | Excessive vibration | 3 | 3 | 2 | 18 | 1083 | 95.25% | NO SCHEDULED MAINTENANCE
Electric Generator | Excessive vibration | 3 | 3 | 2 | 18 | 1101 | 96.83% | NO SCHEDULED MAINTENANCE
Air Inlet | Abnormal instrument reading | 2 | 3 | 2 | 12 | 1113 | 97.89% | NO SCHEDULED MAINTENANCE
Control & Monitoring System | Abnormal instrument reading | 2 | 3 | 2 | 12 | 1125 | 98.94% | NO SCHEDULED MAINTENANCE
Fire & Gas Protection System | Abnormal instrument reading | 2 | 3 | 2 | 12 | 1137 | 100% | NO SCHEDULED MAINTENANCE

## decision diagram (hidden)
| HIDDEN | [6 empty] | SAFETY | [6 empty] | ENVIRONMENT |  |  |  | OPERATION
H | Will the loss of function caused by this failure mode on its own become evident to the operating crew under normal circumstances? (Terdeteksi ato tidak) | [6 empty] | S | Does the failure mode cause a loss of function or other damage which could hurt or kill someone? Kecelakaa atu tdk |  |  |  |  | E | Does the failure mode cause a loss of function or other damage which could breach any known environmental standard or regulation, meggagu lighkuga at tidak |  |  | O | Does the failure mode have a direct adverse effect on operational capability (output, quality, customer service or operating costs in addition to the direct cost of repair)?/ Apakah modus kegagalan memberikan dampak negatif langsung pada kemampuan operasional (output, kualitas, layanan pelanggan atau biaya operasi selain biaya langsung perbaikan)?
[7 empty] | Yes | [5 empty] | No |  |  |  | No | [5 empty] | No
| 1 | [7 empty] | Yes | [6 empty] | Yes
|  |  | No | [17 empty] | Yes
H1 | Is a task to detect whether the failure is occuring or about to occur technically feasible and worth doing? (Ada tidak pemeriksaan) | [8 empty] | S1 | Is a task to detect whether the failure is occuring or about to occur technically feasible and worth doing? | [6 empty] | O1 | Is a task to detect whether the failure is occuring or about to occur technically feasible and worth doing? |  |  |  | N1 | Is a task to detect whether the failure is occuring or about to occur technically feasible and worth doing?
| 2 | Yes | No | [8 empty] | Yes | No | [6 empty] | Yes | No |  |  |  | Yes | No
| Scheduled on-condition task | [9 empty] | Scheduled on-condition task | [7 empty] | Scheduled on-condition task |  |  |  |  | Scheduled on-condition task
H2 | Is a scheduled restoration task to reduce the failure rate technically feasible and worth doing? | [8 empty] | S2 | Is a scheduled restoration task to avoid failures technically feasible and worth doing? | [6 empty] | O2 | Is a scheduled restoration task to reduce the failure rate technically feasible and worth doing? Skedul peraika |  |  |  | N2 | Is a scheduled restoration task to reduce the failure rate technically feasible and worth doing?
|  | Yes | No | [8 empty] | Yes | No | [6 empty] | Yes | No |  |  |  | Yes | No
| Scheduled restoration task | [9 empty] | Scheduled restoration task | [7 empty] | Scheduled restoration task |  |  |  |  | Scheduled restoration task
H3 | Is a scheduled discard task to reduce the failure rate technically feasible and worth doing? | [8 empty] | S3 | Is a scheduled discard task to avoid failures technically feasible and worth doing? | [6 empty] | O3 | Is a scheduled discard task to reduce the failure rate technically feasible and worth doing? Skedul peggatia |  |  |  | N3 | Is a scheduled discard task to reduce the failure rate technically feasible and worth doing?
|  | Yes | No | [8 empty] | Yes | No | [6 empty] | Yes | No |  |  |  | Yes | No
| Scheduled discard task | [9 empty] | Scheduled discard task | [7 empty] | Scheduled discard task |  |  | No scheduled maintenance |  | Scheduled discard task |  |  | No scheduled maintenance
H4 | Is a failure-finding task to detect the failure technically feasible and worth doing? | [8 empty] | S4 | Is a combination of tasks to avoid failures technically feasible and worth doing?
[22 empty] | Redesign may desirable |  |  |  |  | Redesign may desirable
|  | Yes | No | [8 empty] | Yes | No
| Scheduled failure-finding task | [8 empty] | Combination of task |  |  |  |  | Redesign is compulsory
|  |  | H5 | Could the multiple failure affect safety or the environment?
|  | Redesign is compulsory |  | Yes | No | No scheduled maintenance |  | Redesign may desirable
Note on Z3: gigih: Apakah modus kegagalan memberikan dampak negatif langsung pada kemampuan operasional (output, kualitas, layanan pelanggan atau biaya operasi selain biaya langsung perbaikan)?

## RCM Worksheet
RCM WORKSHEET - GAS TURBINE GENERATOR
Referensi Informasi |  | Evaluasi Konsekuensi |  |  |  |  | H1 | H2 | H3 | Tugas Default |  |  | Tugas Proaktif |  | Tugas yang Direkomendasikan | Standar Kinerja | Interval | Teknis | Kategori | Jam Kerja
[7 empty] | S1 | S2 | S3
[7 empty] | E1 | E2 | E3
[7 empty] | O1 | O2 | O3
Komponen | Mode Kegagalan | E | S | E | O | N | N1 | N2 | N3 | H4 | H5 | S4
Kompresor | Kerusakan | Y | Y |  |  |  | N | N | N | N | N | Y | Lakukan tugas kombinasi terjadwal | Lakukan tugas kombinasi terjadwal | 1. Analisis Getaran | Getaran ≤ batas ISO 10816 | Bulanan | PdM | Pemantauan Kondisi | 2
[15 empty] | 2. Pemeriksaan bantalan | Tidak ada kondisi abnormal | 3 Tahun | Mekanik | Pengujian & Inspeksi | 4
[15 empty] | 3. Analisis Oli | Oli: TAN & Viskositas sesuai | Bulanan | PdM | Pemantauan Kondisi | 2
Sistem Pembakaran | Kerusakan | Y | Y |  |  |  | N | N | N | N | N | Y | Lakukan tugas kombinasi terjadwal | Lakukan tugas kombinasi terjadwal | 1. Inspeksi pembakaran | Api stabil dalam 5 detik | 6 Bulan | Instrumen | Pengujian & Inspeksi | 2
[15 empty] | 2. Pemeriksaan termokopel | Kenaikan suhu ≤ spesifikasi | Bulanan | Instrumen | Pemantauan Kondisi | 2
[15 empty] | 3. Uji detektor api | Tidak ada kondisi abnormal | 6 Bulan | Instrumen | Uji Berkala | 2
Peralatan | Mode Kegagalan | E | S | E | O | N | N1 | N2 | N3 | H4 | H5 | S4 | Tugas Default | Tugas Proaktif | Tugas yang Direkomendasikan | Standar Kinerja | Interval | Keahlian | Kategori | Jam Kerja
Kompresor | Kerusakan | Y | Y |  |  | N | N | N | N | N | Y |  | Lakukan tugas kombinasi terjadwal | 1. Analisis getaran | Getaran ≤ batas ISO 10816 | Bulanan | PdM | Pemantauan Kondisi | 2
[14 empty] | 2. Pemeriksaan bantalan | Tidak ada kondisi abnormal | 3 Tahun | Mekanik | Pengujian & Inspeksi | 4
[14 empty] | 3. Analisis oli | Oli: TAN & Viskositas sesuai | Bulanan | PdM | Pemantauan Kondisi | 2
Sistem Pembakaran | Kerusakan | Y | Y |  |  | N | N | N | N | N | Y |  | Lakukan tugas kombinasi terjadwal | 1. Inspeksi pembakaran | Api stabil dalam 5 detik | 6 Bulan | Instrumen | Pengujian & Inspeksi | 2
[14 empty] | 2. Pemeriksaan termokopel | Kenaikan suhu ≤ spesifikasi | Bulanan | Instrumen | Pemantauan Kondisi | 2
[14 empty] | 3. Uji detektor api | Tidak ada kondisi abnormal | 6 Bulan | Instrumen | Uji Berkala | 2
Turbin Daya | Kerusakan | Y | Y |  |  | N | N | N | N | N | Y |  | Lakukan tugas kombinasi terjadwal | 1. Inspeksi visual bilah | Keausan bilah < 10% | Bulanan | Mekanik | Pemantauan Kondisi | 3
[14 empty] | 2. Pemantauan tren getaran | Peningkatan getaran ≤ 10% | Bulanan | PdM | Pemantauan Kondisi | 2
[14 empty] | 3. Pemeriksaan filter oli pelumas | Tidak ada kondisi abnormal | 6 Bulan | Mekanik | Pengujian & Inspeksi | 2
Sistem Transmisi | Kerusakan | Y | Y |  |  | N | N | N | N | N | Y |  | Lakukan tugas kombinasi terjadwal | 1. Analisis oli gearbox | Oli: ISO 4406 ≤ 18/16/13 | Bulanan | PdM | Pemantauan Kondisi | 4
[14 empty] | 2. Pemeriksaan keselarasan | Penyimpangan ≤ 0,1 mm | 3 Tahun | Mekanik | Pengujian & Inspeksi | 4
[14 empty] | 3. Termografi bantalan | Suhu ≤ 90°C | Bulanan | PdM | Pemantauan Kondisi | 2

## RCM Decision Diagram
RCM DECISION DIAGRAM | Y/N
Yes
No

## Simple FMEA
RCM WORKSHEET - GAS TURBINE GENERATOR
Information Reference |  | Recommended Task | Performance Standard | Interval | Craft | Category | Man hours
Equipment | Failure Mode
Combustion | Performance degradation | Temperature monitoring, burner inspection | Temp rise ≤ spec | 6 Monthly | PdM, Instrument | Condition Monitoring | 3
Power Turbine | Performance degradation | Vibration analysis, blade check | Vib trend ≤ ISO | Monthly | PdM | Condition Monitoring | 3
Transmission | Failure to operate | Oil level check, coupling alignment | Oil ≥ min level, alignment ≤ 0.1 mm | 6 Monthly | PdM | Condition Monitoring | 2
Electric Generator | Breakdown | Insulation test, bearing vib check | IR ≥ 1 MΩ, Vib ≤ 4 mm/s | Monthly | Electrical, PdM | Periodic Test | 4
Electric Generator | Power failure | Excitation & AVR test | Voltage build-up within 5s | 6 Monthly | Electrical | Periodic Test | 3
Fuel System | Breakdown | Valve function test, leak test | No leakage, full travel | Monthly | Mechanical | Periodic Test | 3
Fuel System | Failure to operate | Filter cleaning, pressure test | Pressure drop <10% | 6 Monthly | Mechanical | Periodic Test | 2
Fuel System | Performance degradation | Flow rate verification | Flow within ±5% spec | 6 Monthly | Mechanical | Periodic Test | 2
Starting System | Failure to operate | Motor test, battery check | Start < 5s, V ≥ 24V | Monthly | Electrical | Periodic Test | 2
Control & Monitoring System | Control/ signal failure | PLC/SCADA logic test | Signal response < 1s | 6 Monthly | Instrument | Periodic Test | 3
Lubrication System | Breakdown | Pump operation check, pressure test | Pressure ≥ spec | Monthly | Mechanical | Periodic Test | 2
Lubrication System | Failure to operate | Low pressure alarm test | Alarm active <5s | 6 Monthly | Instrument | Periodic Test | 2
Cooling System | Failure to operate | Fan motor test, coolant level | Motor run, coolant ≥ mark | Monthly | Mechanical | Periodic Test | 2
Fire & Gas Protection System | Control/ signal failure | Gas detector calibration, flame test | Alarm/Shutdown OK | Monthly | Instrument | Periodic Test | 3
Exhaust System | Failure to operate | Backpressure check, support inspection | Backpressure ≤ 500 mmWC | 6 Monthly | Mechanical | Testing & Inspection | 2

## Sheet1
KOMPONEN | MODE KEGAGALAN | SEVERITY (S) | OCCURRENCE (O) | DETECTION (D) | RPN | CUMMULATIVE RPN | CUMMULATIVE % RPN
Kompresor | Kerusakan | 8 | 6 | 6 | 288 | 288 | 10.02%
Sistem Pembakaran | Kerusakan | 8 | 6 | 6 | 288 | 576 | 20.04%
Turbin Ekspansi | Kerusakan | 8 | 6 | 6 | 288 | 864 | 30.06%
Transmisi | Kerusakan | 8 | 6 | 6 | 288 | 1152 | 40.08%
Generator Listrik | Gagal Produksi Daya | 8 | 5 | 7 | 280 | 1432 | 49.83%
Sistem Bahan Bakar | Gagal Dioperasikan | 7 | 5 | 7 | 245 | 1677 | 58.35%
Sistem Saluran Udara | Penurunan Kinerja | 7 | 5 | 6 | 210 | 1887 | 65.66%
Sistem Pengaman Kebakaran & Gas | Pembacaan instrument tidak normal | 7 | 6 | 5 | 210 | 2097 | 72.96%
Sistem Pelumasan | Gagal Dioperasikan | 7 | 5 | 5 | 175 | 2272 | 79.05%
Sistem Starter | Gagal Dioperasikan | 7 | 5 | 5 | 175 | 2447 | 85.14%
Sistem Pembuangan Gas | Penurunan Kinerja | 3 | 7 | 7 | 147 | 2594 | 90.26%
Sistem Kontrol & Pemantauan | Pembacaan instrument tidak normal | 5 | 4 | 7 | 140 | 2734 | 95.13%
Sistem Pendingin | Penurunan Kinerja | 5 | 4 | 7 | 140 | 2874 | 100%

## Table S O D
Severity (S)
Skor | Deskripsi | Dampak
5 | Sangat parah | Membahayakan keselamatan jiwa, kegagalan total sistem
4 | Parah | Kegagalan sistem utama, produksi terhenti
3 | Sedang | Penurunan performa, membutuhkan perbaikan besar
2 | Ringan | Masalah dapat ditangani tanpa henti operasi
1 | Sangat ringan | Gangguan kecil, tidak berdampak signifikan terhadap operasi
Occurrence (O)
Skor | Frekuensi Terjadi | Deskripsi
5 | Sangat sering | > sekali seminggu
4 | Sering | 1x per bulan
3 | Kadang-kadang | 1–4x per tahun
2 | Jarang | < 1x per tahun
1 | Sangat jarang | Hampir tidak pernah
Detection (D)
Skor | Kemungkinan Terdeteksi | Deskripsi
5 | Tidak bisa terdeteksi | Tidak ada sistem deteksi sama sekali
4 | Deteksi sangat rendah | Sistem monitoring tidak akurat atau tidak aktif
3 | Deteksi sedang | Ada sistem deteksi tapi tidak selalu berhasil
2 | Deteksi cukup | Sistem deteksi bekerja tetapi tidak real-time
1 | Deteksi tinggi | Sistem deteksi otomatis & real-time (sensor, alarm, shutdown, dll.)

## Table Failure Mode
FAILURE MODE_CATEGORY
NAME | EXAMPLE
Abnormal instrument reading | False alarm, faulty instrument indication
Breakdown | Serious damage (seizure, breakage)
Control-line-to-well communication | Loss of hydraulic control fluids into the well bore
Control/ signal failure | No, or faulty monitoring or regulation, failure to transmit or receive command or data, failure to actuate function
Delayed operation | Opening/closing time below spec.
External leakage – fuel | External leakage of supplied fuel/gas
External leakage - process medium | Oil, gas, condensate, water
External leakage – utility medium | Lubricant, cooling water
Erratic output | Oscillating, hunting, instability
Failure to connect | Failure to connect
Failure to cut | Shear cut valve unable to cut equipment
Failure in lightning protection system | Failure in grounding, insufficient roof thickness, etc.
Faulty output frequency | Wrong/oscillating frequency
Faulty output voltage | Wrong/unstable output voltage
Failure to rotate | Failure to rotate
Failure to close on demand | Doesn’t close on demand
Failure to disconnect | Failure to disconnect upper connector
Failure to function on demand | Doesn’t start on demand, or failure to respond on signal/ activation, or does not respond to input commands; Auxiliary function, subsystem, monitoring or control device fails to operate when demanded
Failure to function as intended | Response not as expected; Protection device/ circuit breaker/ switch fails to clear a fault on the circuit
Failure to lock/unlock | Doesn’t lock or unlock when demanded, failure to connect or disconnect, failure to release SCM from its mounting base
Failure to open on demand | Doesn’t open on demand
Failure to regulate | Fails to control the load, poor response to feedback
Failure to start on demand | Doesn’t start on demand
Failure while running | Unable to run equipment or tools
High output | Output torque above specifications
Heating failure | Loss of ability to provide heating
Insufficient heat transfer | Lack off or reduced ability to transfer heat from hot temperature areas, such as power transformers or power supply electronics
Internal leakage - process medium | Leakage process medium going through heat coils or similar.
Internal leakage - utility medium | Leakage internally of utility fluids
Internal leakage | Leakage internally of process or utility fluids
Low oil supply pressure | Low oil supply pressure
Leakage in closed position | Leakage through a valve (e.g. ram-valve) in closed position
Load drop | Load drop
Loss of buoyancy | Loss of buoyancy in idle position
Low output | Performance below specifications
Mooring failure | Mooring failure
Noise | Excessive noise
No output | No output
Overheating | Machine parts, exhaust, cooling water, etc.
Other | Failure modes not covered above
Premature closure | Spurious closure of valve without command
Parameter deviation | Monitored parameter exceeding limits, e.g. high/low alarm
` | Partly or full flow restriction due to hydrate, scale, wax, etc.
Loss of functions on both pods | Both pods are not functioning as desired
Insufficient power | Lack of or too low power supply
Power/signal transmission failure | Power/signal transmission failure
Sludge build-up | Sludge build-up
Minor in-service problems | Loose items, discoloration, dirt
Failure to set/retrieve | Failed set/retrieve operations
Spurious high alarm level | e.g. 60 % of Lower Explosive Limit (LEL)
Spurious low alarm level | e.g. 20 % of Lower Explosive Limit (LEL)
Slippage | Wire slippage
Spurious operation | e.g. false alarm; Undesired opening; Fails to operate as demanded, false alarm, premature closure/stop, unexpected operation/fails to operate as demanded
Structural deficiency | Material damages (cracks, wear, fracture, corrosion), reduced integrity
Failure to stop on demand | Doesn’t stop on demand
Stuck | Tools becoming stuck in the BOP or X-mas Tree
Global buckling | Upheaval or lateral buckling
Unknown | Too little information to define a failure mode
Spurious stop | Unexpected shutdown
Vibration | Abnormal/excessive vibration
Very low output | e.g. reading between 11 % LEL to 30 % Lower Explosive Limit (LEL) upon test gas.
Well-to-control-line communication | Influx of well fluids into valve control line