## WO
No | No. Work Order | Description | Asset
1 | 202418730 | OH SI INSPEKSI TURBIN-GENERATOR UNIT 1 | AA01MAA10-001
2 | 202419688 | [UNIT 3][SAH][MOTOR EMERGENCY SAH][NOISE PADA MOTOR EMERGENCY SAH] | AA03HLD20-001
3 | 202415012 | [UNIT3][BOILER][TUBE BOILER][BOCOR] | AA03HBB10AG001-001
4 | 202415012 | [UNIT3][BOILER][TUBE BOILER][BOCOR] | AA03HBB10AG001-001
5 | 202315308 | [Unit 2] [Turbin] [Blade Turbin stage 14] [Reblading] | AA02MAA10HB001-001
6 | 202315308 | [Unit 2] [Turbin] [Blade Turbin stage 14] [Reblading] | AA02MAA10HB001-001
7 | 2023144928 | [Unit 3] [Turbin System] [Gen#1bearing bush vibrasi Horizontal] [Error] | AA03UMA03
8 | 2024126688 | [Unit 4] [Vacuum Pump A] [Seal Water Pompa] [Bocor] | AA04UMA03
9 | 202315308 | [Unit 2] [Turbin] [Blade Turbin stage 14] [Reblading] | AA02MAA10HB001-001
10 | 202419569 | UNIT 4][VALVE MANUAL DRINE SUPER HEATER][SHAFT ULIR BERKARAT DAN BERAT SAAT DI MANUVER] | AA04MAA20-001

## Failure Mode
FAILURE MODE TURBINE GENERATOR
No | Component/Equipment | Sub-Component | Failure Mode | Failure Cause | Failure Effects | Severity (S) | Occurrence (O) | Detection (D) | RPN
1 | Turbine | Blades | Mech-General | General | Crack pada Blade | 9 | 3 | 5 | 100
2 | Turbine | Blades | Mech-Leakage | Improper material | Kebocoran Steam | 9 | 3 | 5 | 100
3 | Turbine | Blades | Mech-Deformation | Operation error | Penurunan perfoma Blade | 9 | 3 | 5 | 100
4 | Turbine | Blades | Mech-Looseness | Maintenance error | Unballance | 9 | 3 | 5 | 100
5 | Turbine | Blades | Mech-Clearence/Allignment | Misce-Other | Lifetime Blade | 9 | 3 | 5 | 100
6 | Turbine | Bearings | Mech-General | General | Crack pada Bearing | 9 | 5 | 3 | 80
7 | Turbine | Bearings | Mech-Leakage | Maintenance error | Bearing Aus | 9 | 5 | 3 | 80
8 | Turbine | Bearings | Mech-Deformation | Misce-Other | Lifetime | 9 | 5 | 3 | 80
9 | Turbine | Bearings | Mech-Looseness | Op/Maintenance Error | PM pelumasan dan monitoring tidak efektif | 9 | 5 | 3 | 80
10 | Turbine | Shaft Turbin | Mech-Clearence/Allignment | Op/Maintenance Error | Bending pada Shaft | 9 | 3 | 5 | 100
11 | Turbine | Shaft Turbin | Mech-Leakage | Expected wear and tear | Kebocoran seal dan packing | 9 | 3 | 5 | 100
12 | Turbine | Shaft Turbin | Mech-Looseness | Improper material | Unballance | 9 | 3 | 5 | 100
13 | Turbine | Thrust Bearing | Mech-General | General | Crack pada Bearing | 7 | 3 | 3 | 70
14 | Turbine | Thrust Bearing | Mech-Leakage | Op/Maintenance Error | Bearing Aus | 7 | 5 | 3 | 70
15 | Turbine | Thrust Bearing | Mech-Looseness | Misce-Other | Lifetime | 7 | 5 | 3 | 70
16 | Turbine | Front Standart | Mech-General | General | Crack pada Chasing | 7 | 5 | 3 | 70
17 | Turbine | Front Standart | Mech-Leakage | Op/Maintenance Error | Lifetime | 7 | 5 | 3 | 70
18 | Turbine | Front Standart | Mech-Looseness | Misce-Other | Kebocoran pada packing | 7 | 5 | 3 | 70
19 | Turbine | Control Valve | Mech-General | General | Control Valve Cekat / tidak bisa dimanuver | 9 | 5 | 5 | 100
20 | Turbine | Control Valve | Mech-Leakage | Op/Maintenance Error | Seal pelumas Disc bocor | 9 | 5 | 5 | 100
21 | Turbine | Control Valve | Mech-Deformation | Misce-Other | Lifetime | 9 | 5 | 5 | 60
22 | Turbine | HP Blade | Mech-General | General | Improper design material | 6 | 5 | 3 | 60
23 | Turbine | HP Blade | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 6 | 5 | 3 | 60
24 | Turbine | HP Blade | Mech-Looseness | Misce-Other | Lifetime | 6 | 5 | 3 | 60
25 | Turbine | HP Nozzle | Mech-General | General | Improper design material | 6 | 5 | 3 | 60
26 | Turbine | HP Nozzle | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 6 | 5 | 3 | 60
27 | Turbine | HP Nozzle | Mech-Looseness | Misce-Other | Lifetime | 6 | 5 | 3 | 60
28 | Turbine | HP Chasing | Mech-General | General | Improper design material | 6 | 5 | 3 | 60
29 | Turbine | HP Chasing | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 5 | 5 | 3 | 60
30 | Turbine | HP Chasing | Mech-Looseness | Misce-Other | Lifetime | 5 | 5 | 3 | 60
31 | Turbine | Turbine Rotor | Mech-Clearence/Allignment | Op/Maintenance Error | Bending pada Rotor Shaft | 5 | 3 | 5 | 100
32 | Turbine | Turbine Rotor | Mech-Leakage | Expected wear and tear | Unballance | 9 | 3 | 5 | 100
33 | Turbine | Turbine Rotor | Mech-Looseness | Misce-Other | Lifetime | 9 | 3 | 5 | 100
34 | Turbine | Diaphragm | Mech-General | General | Improper design material | 9 | 5 | 3 | 70
35 | Turbine | Diaphragm | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 7 | 5 | 3 | 70
36 | Turbine | Diaphragm | Mech-Looseness | Misce-Other | Lifetime | 7 | 5 | 3 | 70
37 | Turbine | LP Blade | Mech-General | General | Improper design material | 7 | 5 | 3 | 60
38 | Turbine | LP Blade | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 5 | 5 | 3 | 60
39 | Turbine | LP Blade | Mech-Looseness | Misce-Other | Lifetime | 5 | 5 | 3 | 60
40 | Turbine | Lp Nozzle | Mech-General | General | Improper design material | 5 | 5 | 3 | 60
41 | Turbine | Lp Nozzle | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 5 | 5 | 3 | 60
42 | Turbine | Lp Nozzle | Mech-Looseness | Misce-Other | Lifetime | 5 | 5 | 3 | 60
43 | Turbine | LP Chasing | Mech-General | General | Improper design material | 5 | 5 | 3 | 60
44 | Turbine | LP Chasing | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 5 | 5 | 3 | 60
45 | Turbine | LP Chasing | Mech-Looseness | Misce-Other | Lifetime | 5 | 5 | 3 | 60
46 | Turbine | Turning Gear | Mech-General | General | Turning Gear Cekat | 9 | 3 | 3 | 100
47 | Turbine | Turning Gear | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 9 | 3 | 5 | 100
48 | Turbine | Turning Gear | Mech-Looseness | Misce-Other | Lifetime | 9 | 3 | 5 | 100
49 | Turbine | Exhaust Spray | Mech-General | General | Improper design material | 5 | 5 | 5 | 70
50 | Turbine | Exhaust Spray | Mech-Leakage | Op/Maintenance Error | Kebocoran seal dan packing | 5 | 5 | 5 | 70
51 | Turbine | Exhaust Spray | Mech-Looseness | Misce-Other | Lifetime | 5 | 5 | 3 | 70
52 | Turbine | LP Packing | Mech-General | General | Improper design material | 5 | 5 | 3 | 70
53 | Turbine | LP Packing | Mech-Leakage | Op/Maintenance Error | Pemasangan tidak akurat | 5 | 5 | 3 | 70
54 | Turbine | LP Packing | Mech-Looseness | Misce-Other | Lifetime | 5 | 5 | 3 | 70
55 | Generator | Windings Exciter | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 9 | 5 | 5 | 100
56 | Generator | Windings Exciter | Elc-Short Circuit | Op/Maintenance Error | Short pada belitan | 9 | 5 | 5 | 100
57 | Generator | Windings Exciter | Misce-Other | Other | Lifetime | 9 | 5 | 5 | 100
58 | Generator | Rotor Exciter | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 9 | 5 | 5 | 100
59 | Generator | Rotor Exciter | Elc-Short Circuit | Op/Maintenance Error | Short pada belitan | 9 | 5 | 5 | 100
60 | Generator | Rotor Exciter | Misce-Other | Other | Lifetime | 9 | 5 | 5 | 100
61 | Generator | Bearings | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 7 | 5 | 3 | 70
62 | Generator | Bearings | Corrosion | Op/Maintenance Error | Bearing Aus | 7 | 5 | 3 | 70
63 | Generator | Bearings | Misce-Other | Other | Lifetime | 7 | 5 | 3 | 70
64 | Generator | Kabel Listrik | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 7 | 3 | 3 | 50
65 | Generator | Kabel Listrik | Elc-Short Circuit | Op/Maintenance Error | Kabel short | 7 | 3 | 3 | 50
66 | Generator | Kabel Listrik | Misce-Other | Other | Lifetime | 7 | 3 | 3 | 50
67 | Generator | Cooler | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 5 | 5 | 5 | 70
68 | Generator | Cooler | Thermal Cycling | Op/Maintenance Error | PM tidak berjalan optimal | 5 | 5 | 5 | 70
69 | Generator | Cooler | Misce-Other | Other | Lifetime | 5 | 5 | 5 | 70
70 | Generator | Excitter | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 9 | 5 | 3 | 90
71 | Generator | Excitter | Elc-Short Circuit | Op/Maintenance Error | Short pada belitan | 9 | 5 | 3 | 90
72 | Generator | Excitter | Misce-Other | Other | Lifetime | 9 | 5 | 3 | 90
73 | Generator | Coil | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 9 | 5 | 5 | 100
74 | Generator | Coil | Elc-Short Circuit | Op/Maintenance Error | Short pada belitan | 9 | 5 | 5 | 100
75 | Generator | Coil | Misce-Other | Other | Lifetime | 9 | 5 | 5 | 100
76 | Generator | Shaft | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 9 | 5 | 7 | 100
77 | Generator | Shaft | Mech-Clearence/Allignment | Op/Maintenance Error | Bending pada Shaft | 9 | 5 | 7 | 100
78 | Generator | Shaft | Misce-Other | Other | Lifetime | 9 | 5 | 7 | 100
79 | Generator | Rotor Winding | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 9 | 5 | 5 | 90
80 | Generator | Rotor Winding | Elc-Short Circuit | Op/Maintenance Error | Short pada belitan | 9 | 5 | 5 | 90
81 | Generator | Rotor Winding | Misce-Other | Other | Lifetime | 9 | 5 | 5 | 90
82 | Generator | Stator Winding | Elc-General | General | Desain atau konfigurasi peralatan yang tidak memadai | 9 | 5 | 5 | 90
83 | Generator | Stator Winding | Elc-Short Circuit | Op/Maintenance Error | Short pada belitan | 9 | 5 | 5 | 90
84 | Generator | Stator Winding | Misce-Other | Other | Lifetime | 9 | 5 | 5 | 90

## Operation Data
TIME EVENT START | EVENT STATUS | EVENT DETAIL | SYSTEM/EQUIPMENT CAUSE CODE | FAILURE MODE | ACTION | POWER REALIZATION |  | TIME EVENT STOP | EVENT IMPACT | POWER LOSS OUTPUT (MW) |  | DURATION |  |  |  | ENERGY LOSS OUTPUT (MWH) |  | RCFA | BULAN KE- | BARIS KE-
[6 empty] | BRUTO (MW) | NETO (TRANSFER) (MW) |  |  | OEE CALC (GMC BASE) | NERC PERF CALC (NMC BASE) | TIME | HOUR | EQUIVALENT HOUR (GMC BASE) | EQUIVALENT HOUR (NMC BASE) | OEE CALC (GMC BASE) | NERC PERF CALC (NMC BASE)
2024-01-01 | FD | Penormalan Parameter pasca Sinkron | 9999 Total unit performance testing (use appropriate codes for individual component testing) - Performance - Performance | F530 Inspection | Kenaikan beban bertahap | 34.6828 | 31.39 | 2024-01-01 05:00 | Derating | 30.3172 | 22.61 | 0 day 5:00 | 5 | 2.3321 | 2.0935 | 151.5859 |  |  | 1 | 5
2024-01-01 05:00 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.6646 | 54 | 2024-01-26 09:33 | Derating | 5.3354 | 0 | 25 day 4:33 | 604.55 | 49.6233 | 0 | 3225.5161 | 0 |  | 1 | 6
2024-01-26 09:33 | MD | Noise Motor coal Feeder 2A Abnormal | 253 Pulverizer feeder motor - Boiler Fuel Supply from Bunkers to Boiler - Boiler | F620 Noisy | Change Mill 2A ke 2B | 24.0868 | 21.8 | 2024-01-26 11:10 | Derating | 40.9132 | 32.2 | 0 day 1:37 | 1.6167 | 1.0176 | 0.96401 | 66.143 | 52.0567 |  | 1 | 7
2024-01-26 11:10 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.6646 | 54 | 2024-02-01 | Derating | 5.3354 | 0 | 5 day 12:50 | 132.8333 | 10.9034 | 0 | 708.719 | 0 |  | 1 | 8
2024-02-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 52.5242 | 47.09 | 2024-02-01 13:20 | Derating | 12.4758 | 6.91 | 0 day 13:20 | 13.3333 | 2.5591 | 1.7062 | 166.3442 | 92.1333 |  | 2 | 9
2024-02-01 13:20 | FD | Vibrasi Mill 2B, Change mill 2B ke 2C | 310 Pulverizer mills - Boiler Fuel Supply from Bunkers to Boiler - Boiler | F860 Vibration fatigue, leading to failure | Rencana Perbaikan inner Part Mill | 22.0626 | 19.78 | 2024-02-01 15:15 | Derating | 42.9374 | 34.22 | 0 day 1:55 | 1.9167 | 1.2661 | 1.2146 | 82.2967 | 65.5883 |  | 2 | 10
2024-02-01 15:15 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.4577 | 49.72 | 2024-02-09 03:00 | Derating | 9.5423 | 4.28 | 7 day 11:45 | 179.75 | 26.3882 | 14.2469 | 1715.2306 | 769.33 |  | 2 | 11
2024-02-09 07:25 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.8665 | 49.19 | 2024-02-09 22:14 | Derating | 10.1335 | 4.81 | 0 day 14:49 | 14.8167 | 2.3099 | 1.3198 | 150.1443 | 71.2682 |  | 2 | 12
2024-02-10 10:07 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.9 | 49.22 | 2024-02-10 22:55 | Derating | 10.1 | 4.78 | 0 day 12:48 | 12.8 | 1.9889 | 1.133 | 129.2802 | 61.184 |  | 2 | 13
2024-02-11 10:21 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.2681 | 49.55 | 2024-02-11 23:05 | Derating | 9.7319 | 4.45 | 0 day 12:44 | 12.7333 | 1.9065 | 1.0493 | 123.9199 | 56.6633 |  | 2 | 14
2024-02-12 09:46 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.0785 | 49.38 | 2024-02-12 23:05 | Derating | 9.9215 | 4.62 | 0 day 13:19 | 13.3167 | 2.0326 | 1.1393 | 132.1219 | 61.523 |  | 2 | 15
2024-02-13 08:13 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.1677 | 49.46 | 2024-02-14 01:02 | Derating | 9.8323 | 4.54 | 0 day 16:49 | 16.8167 | 2.5438 | 1.4138 | 165.3468 | 76.3477 |  | 2 | 16
2024-02-14 11:15 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.5431 | 48.9 | 2024-02-15 21:52 | Derating | 10.4569 | 5.1 | 1 day 10:37 | 34.6167 | 5.569 | 3.2694 | 361.9844 | 176.545 |  | 2 | 17
2024-02-15 21:52 | FD | Indikasi blocking Mill 2C DP Mill high | 310 Pulverizer mills - Boiler Fuel Supply from Bunkers to Boiler - Boiler | F690 Seized (not moving) | Turun coal flow dan turun beban | 51.9107 | 46.54 | 2024-02-16 01:30 | Derating | 13.0893 | 7.46 | 0 day 3:38 | 3.6333 | 0.73166 | 0.50194 | 47.5577 | 27.1047 |  | 2 | 18
2024-02-16 01:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.5319 | 48.89 | 2024-02-25 06:35 | Derating | 10.4681 | 5.11 | 9 day 5:05 | 221.0833 | 35.6049 | 20.921 | 2314.3211 | 1129.7358 |  | 2 | 19
2024-02-25 08:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.1638 | 48.56 | 2024-02-26 02:55 | Derating | 10.8362 | 5.44 | 0 day 18:25 | 18.4167 | 3.0702 | 1.8553 | 199.5662 | 100.1867 |  | 2 | 20
2024-02-26 07:45 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.4315 | 48.8 | 2024-02-26 13:23 | Derating | 10.5685 | 5.2 | 0 day 5:38 | 5.6333 | 0.91593 | 0.54247 | 59.5358 | 29.2933 |  | 2 | 21
2024-02-26 13:23 | FD | Pipa HPU Mill 2C Pecah | 340 Other pulverizer problems - Boiler Fuel Supply from Bunkers to Boiler - Boiler | F540 Leaks | Stop Mill untuk Penggantian Line Pipa HPU Mill 2C | 28.5319 | 25.58 | 2024-02-26 21:30 | Derating | 36.4681 | 28.42 | 0 day 8:07 | 8.1167 | 4.5538 | 4.2718 | 295.9992 | 230.6757 |  | 2 | 22
2024-02-26 21:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 53.9073 | 48.33 | 2024-02-26 22:49 | Derating | 11.0927 | 5.67 | 0 day 1:19 | 1.3167 | 0.2247 | 0.13825 | 14.6054 | 7.4655 |  | 2 | 23
2024-02-27 08:00 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.2792 | 49.56 | 2024-02-28 02:30 | Derating | 9.7208 | 4.44 | 0 day 18:30 | 18.5 | 2.7667 | 1.5211 | 179.8344 | 82.14 |  | 2 | 24
2024-02-28 08:03 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.8219 | 49.15 | 2024-02-29 07:00 | Derating | 10.1781 | 4.85 | 0 day 22:57 | 22.95 | 3.5936 | 2.0612 | 233.5872 | 111.3075 |  | 2 | 25
2024-02-29 07:41 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.1119 | 49.41 | 2024-03-01 | Derating | 9.8881 | 4.59 | 0 day 16:19 | 16.3167 | 2.4822 | 1.3869 | 161.3406 | 74.8935 |  | 2 | 26
2024-03-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.5314 | 49.52 | 2024-03-02 06:56 | Derating | 10.4686 | 4.48 | 1 day 6:56 | 30.9333 | 4.982 | 2.5663 | 323.828 | 138.5813 |  | 3 | 27
2024-03-02 08:45 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.4564 | 50.36 | 2024-03-30 06:18 | Derating | 9.5436 | 3.64 | 27 day 21:33 | 669.55 | 98.3061 | 45.1326 | 6389.896 | 2437.162 |  | 3 | 28
2024-03-30 07:40 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.1921 | 50.12 | 2024-04-01 | Derating | 9.8079 | 3.88 | 1 day 16:20 | 40.3333 | 6.0859 | 2.898 | 395.5835 | 156.4933 |  | 3 | 29
2024-04-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.3133 | 50.23 | 2024-04-09 23:40 | Derating | 9.6867 | 3.77 | 8 day 23:40 | 215.6667 | 32.1401 | 15.0567 | 2089.1035 | 813.0633 |  | 4 | 30
2024-04-15 07:40 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.6085 | 49.59 | 2024-04-26 15:55 | Derating | 10.3915 | 4.41 | 11 day 8:15 | 272.25 | 43.5244 | 22.2337 | 2829.0837 | 1200.6225 |  | 4 | 31
2024-04-26 15:55 | FO | Level CCST error, Trip Vacuum LowLow, Separator vacum pump Low | 3360 Condensate makeup and return (including storage tanks) - Condensate System - Balance of Plant | F430 Error, wiring | Penormalan Level CCST | 0 | 0 | 2024-04-27 03:36 | Trip | 65 | 54 | 0 day 11:41 | 11.6833 | 11.6833 | 11.6833 | 759.4167 | 630.9 |  | 4 | 32
2024-04-27 12:59 | FO | Level Drum Low Low, BFP 2A abnormal, DP BFP tinggi | 3407 Feedwater pump suction screens - Feedwater System - Balance of Plant | F320 Dirty (use for air contamination or particulate/dirt buildup) | Cleaning Filter Inlet BFP | 0 | 0 | 2024-04-28 01:19 | Trip | 65 | 54 | 0 day 12:20 | 12.3333 | 12.3333 | 12.3333 | 801.6667 | 666 |  | 4 | 33
2024-04-30 08:20 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.2011 | 49.22 | 2024-05-01 | Derating | 10.7989 | 4.78 | 0 day 15:40 | 15.6667 | 2.6028 | 1.3868 | 169.1833 | 74.8867 |  | 4 | 34
2024-05-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.5171 | 49.48 | 2024-05-05 01:05 | Derating | 10.4829 | 4.52 | 4 day 1:05 | 97.0833 | 15.6572 | 8.1262 | 1017.7184 | 438.8167 |  | 5 | 35
2024-05-05 01:05 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.4972 | 54 | 2024-05-13 | Derating | 5.5028 | 0 | 7 day 22:55 | 190.9167 | 16.1627 | 0 | 1050.5762 | 0 |  | 5 | 36
2024-05-13 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 49.581 | 45 | 2024-05-13 05:35 | Derating | 15.419 | 9 | 0 day 5:35 | 5.5833 | 1.3245 | 0.93056 | 86.0894 | 50.25 |  | 5 | 37
2024-05-14 08:00 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 55.3104 | 50.2 | 2024-05-25 03:06 | Derating | 9.6896 | 3.8 | 10 day 19:06 | 259.1 | 38.6244 | 18.233 | 2510.5857 | 984.58 |  | 5 | 38
2024-05-25 10:29 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 55.2332 | 50.13 | 2024-05-30 11:06 | Derating | 9.7668 | 3.87 | 5 day 0:37 | 120.6167 | 18.1236 | 8.6442 | 1178.0348 | 466.7865 |  | 5 | 39
2024-05-30 11:06 | FD | Kendala Server DCS Coal Handling | 3970 Distributive Control System (DCS) - process computer - Miscellaneous (Balance of Plant) - Balance of Plant | F520 Indication, false | Reset Server DCS Coal Handling | 47.2011 | 42.84 | 2024-05-30 22:30 | Derating | 17.7989 | 11.16 | 0 day 11:24 | 11.4 | 3.1217 | 2.356 | 202.9073 | 127.224 |  | 5 | 40
2024-05-30 22:30 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.462 | 49.43 | 2024-06-01 | Derating | 10.538 | 4.57 | 1 day 1:30 | 25.5 | 4.1341 | 2.1581 | 268.7197 | 116.535 |  | 5 | 41
2024-06-01 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.4437 | 49.4 | 2024-06-05 00:57 | Derating | 10.5563 | 4.6 | 4 day 0:57 | 96.95 | 15.7451 | 8.2587 | 1023.4294 | 445.97 |  | 6 | 42
2024-06-05 08:00 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.058 | 49.05 | 2024-06-06 00:19 | Derating | 10.942 | 4.95 | 0 day 16:19 | 16.3167 | 2.7467 | 1.4957 | 178.5369 | 80.7675 |  | 6 | 43
2024-06-06 08:11 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.7193 | 49.65 | 2024-06-16 23:37 | Derating | 10.2807 | 4.35 | 10 day 15:26 | 255.4333 | 40.4007 | 20.5766 | 2626.0424 | 1111.135 |  | 6 | 44
2024-06-17 16:22 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 55.105 | 50 | 2024-06-18 03:36 | Derating | 9.895 | 4 | 0 day 11:14 | 11.2333 | 1.7101 | 0.8321 | 111.1538 | 44.9333 |  | 6 | 45
2024-06-18 09:00 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 55.8765 | 50.7 | 2024-06-19 03:00 | Derating | 9.1235 | 3.3 | 0 day 18:00 | 18 | 2.5265 | 1.1 | 164.2235 | 59.4 |  | 6 | 46
2024-06-19 06:30 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 55.8324 | 50.66 | 2024-06-29 05:16 | Derating | 9.1676 | 3.34 | 9 day 22:46 | 238.7667 | 33.6757 | 14.7682 | 2188.9206 | 797.4807 |  | 6 | 47
2024-06-29 09:59 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 55.8103 | 50.64 | 2024-07-01 | Derating | 9.1897 | 3.36 | 1 day 14:01 | 38.0167 | 5.3748 | 2.3655 | 349.3601 | 127.736 |  | 6 | 48
2024-07-01 08:18 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 53.1899 | 48.04 | 2024-07-01 23:04 | Derating | 11.8101 | 5.96 | 0 day 14:46 | 14.7667 | 2.683 | 1.6298 | 174.396 | 88.0093 |  | 7 | 49
2024-07-03 17:00 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.0203 | 48.79 | 2024-07-03 23:17 | Derating | 10.9797 | 5.21 | 0 day 6:17 | 6.2833 | 1.0614 | 0.60623 | 68.9892 | 32.7362 |  | 7 | 50
2024-07-04 11:15 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.3967 | 49.13 | 2024-07-04 22:35 | Derating | 10.6033 | 4.87 | 0 day 11:20 | 11.3333 | 1.8488 | 1.0221 | 120.1703 | 55.1933 |  | 7 | 51
2024-07-05 08:52 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.9503 | 49.63 | 2024-07-05 22:34 | Derating | 10.0497 | 4.37 | 0 day 13:42 | 13.7 | 2.1182 | 1.1087 | 137.6804 | 59.869 |  | 7 | 52
2024-07-06 17:20 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 52.7249 | 47.62 | 2024-07-06 21:30 | Derating | 12.2751 | 6.38 | 0 day 4:10 | 4.1667 | 0.78687 | 0.49228 | 51.1464 | 26.5833 |  | 7 | 53
2024-07-08 11:18 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 55.2714 | 49.92 | 2024-07-11 02:05 | Derating | 9.7286 | 4.08 | 2 day 14:47 | 62.7833 | 9.3968 | 4.7436 | 610.7924 | 256.156 |  | 7 | 54
2024-07-11 13:30 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.8285 | 49.52 | 2024-07-11 23:30 | Derating | 10.1715 | 4.48 | 0 day 10:00 | 10 | 1.5648 | 0.82963 | 101.7146 | 44.8 |  | 7 | 55
2024-07-12 06:01 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.6957 | 49.4 | 2024-07-13 23:31 | Derating | 10.3043 | 4.6 | 1 day 17:30 | 41.5 | 6.5789 | 3.5352 | 427.6293 | 190.9 |  | 7 | 56
2024-07-13 23:31 | FO | BPS dan BMS CPU Control Error, berakibat kontrol boiler tidak dapat di lakukan | 1750 Burner management system - Boiler Control Systems - Boiler | F430 Error, wiring | Rencana penggantian BPS dan BMS saat OH | 0 | 0 | 2024-07-14 07:33 | Trip | 65 | 54 | 0 day 8:02 | 8.0333 | 8.0333 | 8.0333 | 522.1667 | 433.8 |  | 7 | 57
2024-07-14 08:33 | FD | BPS dan BMS CPU Control Error, berakibat kontrol boiler tidak dapat di lakukan | 1750 Burner management system - Boiler Control Systems - Boiler | F430 Error, wiring | Rencana penggantian BPS dan BMS saat OH | 40.8557 | 36.9 | 2024-07-15 06:00 | Derating | 24.1443 | 17.1 | 0 day 21:27 | 21.45 | 7.9676 | 6.7925 | 517.8957 | 366.795 |  | 7 | 58
2024-07-15 06:00 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 53.7546 | 48.55 | 2024-07-16 08:15 | Derating | 11.2454 | 5.45 | 1 day 2:15 | 26.25 | 4.5414 | 2.6493 | 295.1928 | 143.0625 |  | 7 | 59
2024-07-18 14:00 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 53.976 | 48.75 | 2024-07-21 00:46 | Derating | 11.024 | 5.25 | 2 day 10:46 | 58.7667 | 9.9668 | 5.7134 | 647.8437 | 308.525 |  | 7 | 60
2024-07-21 09:09 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 54.5296 | 49.25 | 2024-07-23 01:20 | Derating | 10.4704 | 4.75 | 1 day 16:11 | 40.1833 | 6.4729 | 3.5346 | 420.7356 | 190.8708 |  | 7 | 61
2024-07-23 01:20 | FD | Gangguan FDF 2B, Motor running tapi Fan tidak berputar, indikasi Lepas Kopling | 1413 Forced draft fan couplings - Boiler Air and Gas Systems - Boiler | F060 Broken | Penggantian Kopling FDF 2B | 36.7701 | 33.21 | 2024-07-23 22:58 | Derating | 28.2299 | 20.79 | 0 day 21:38 | 21.6333 | 9.3955 | 8.3288 | 610.7066 | 449.757 |  | 7 | 62
2024-07-23 22:58 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 55.1939 | 49.85 | 2024-07-26 23:40 | Derating | 9.8061 | 4.15 | 3 day 0:42 | 72.7 | 10.9677 | 5.5871 | 712.902 | 301.705 |  | 7 | 63
2024-07-27 18:33 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 53.5553 | 48.37 | 2024-07-28 21:12 | Derating | 11.4447 | 5.63 | 1 day 2:39 | 26.65 | 4.6923 | 2.7785 | 305.0022 | 150.0395 |  | 7 | 64
2024-07-28 21:12 | FO | BPS dan BMS CPU Control Error, berakibat kontrol boiler tidak dapat di lakukan | 1750 Burner management system - Boiler Control Systems - Boiler | F430 Error, wiring | Rencana penggantian BPS dan BMS saat OH | 0 | 0 | 2024-07-29 05:45 | Trip | 65 | 54 | 0 day 8:33 | 8.55 | 8.55 | 8.55 | 555.75 | 461.7 |  | 7 | 65
2024-07-29 07:00 | FD | BPS dan BMS CPU Control Error, berakibat kontrol boiler tidak dapat di lakukan | 1750 Burner management system - Boiler Control Systems - Boiler | F430 Error, wiring | Rencana penggantian BPS dan BMS saat OH | 14.7258 | 13.3 | 2024-07-29 10:10 | Derating | 50.2742 | 40.7 | 0 day 3:10 | 3.1667 | 2.4493 | 2.3867 | 159.2018 | 128.8833 |  | 7 | 66
2024-07-29 14:07 | MD | Monitoring Generator Winding Temp High | 4520 Stator windings, bushings, and terminals - Generator - Generator | F780 Temperature - general, not within limits | Rencana Cleaning Cooler Saat OH | 53.4224 | 48.25 | 2024-08-01 | Derating | 11.5776 | 5.75 | 2 day 9:53 | 57.8833 | 10.31 | 6.1635 | 670.1501 | 332.8292 |  | 7 | 67
2024-08-01 00:20 | PO | Serious Inspection Plus selama 60 hari | 4401 Inspection - Miscellaneous (Steam Turbine) - Steam Turbine | F530 Inspection |  | 0 | 0 | 2024-09-01 | Shutdown | 65 | 54 | 30 day 23:40 | 743.6667 | 743.6667 | 743.6667 | 48338.3333 | 40158 |  | 8 | 68
2024-09-01 | PO | Serious Inspection Plus selama 60 hari | 4401 Inspection - Miscellaneous (Steam Turbine) - Steam Turbine | F530 Inspection |  | 0 | 0 | 2024-09-23 23:59 | Shutdown | 65 | 54 | 22 day 23:59 | 551.9833 | 551.9833 | 551.9833 | 35878.9167 | 29807.1 |  | 9 | 69
2024-09-23 23:59 | MD | Monitoring Main Steam Temperature High | 500 Main steam piping up to turbine stop valves - Boiler Piping System - Boiler | F290 Creep, high temperature | Melakukan Combustion Tunning | 56.523 | 51.45 | 2024-09-27 18:00 | Derating | 8.477 | 2.55 | 3 day 18:01 | 90.0167 | 11.7396 | 4.2508 | 763.074 | 229.5425 |  | 9 | 70
2024-09-27 18:00 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.3244 | 54 | 2024-10-01 | Derating | 5.6756 | 0 | 3 day 6:00 | 78 | 6.8107 | 0 | 442.6968 | 0 |  | 9 | 71
2024-10-01 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-10-02 11:27 | Derating | 5.897 | 0 | 1 day 11:27 | 35.45 | 3.2161 | 0 | 209.0486 | 0 |  | 10 | 72
2024-10-02 11:27 | FD | Coal Feeder 2B Trip | 250 Pulverizer feeders - Boiler Fuel Supply from Bunkers to Boiler - Boiler | F820 Tripped/shutdown component - automatic controls | Pergantian sensor Tachometer 2B | 36.3593 | 33.22 | 2024-10-02 19:00 | Derating | 28.6407 | 20.78 | 0 day 7:33 | 7.55 | 3.3267 | 2.9054 | 216.2374 | 156.889 |  | 10 | 73
2024-10-02 19:00 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-10-20 07:09 | Derating | 5.897 | 0 | 17 day 12:09 | 420.15 | 38.1173 | 0 | 2477.6246 | 0 |  | 10 | 74
2024-10-20 07:09 | FO | Unit Trip - Sinyal Turbin Speed Error muncul karena modul F1-TP01 dan F3-TP01 Failure 2 out of 3. | 4311 Steam Turbine Control System - hardware problems (including card failure) - Controls - Steam Turbine | F410 Erratic, circuit | Penormalan modul F1-TP01 & F3-TP01 Failure 2 out of 3 dengan tindakan reset dan memastikan input sinyal dari sensor Turbin Speed - Start Up Unit | 0 | 0 | 2024-10-20 14:07 | Trip | 65 | 54 | 0 day 6:58 | 6.9667 | 6.9667 | 6.9667 | 452.8333 | 376.2 |  | 10 | 75
2024-10-20 14:07 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-10-22 07:53 | Derating | 5.897 | 0 | 1 day 17:46 | 41.7667 | 3.7892 | 0 | 246.298 | 0 |  | 10 | 76
2024-10-22 07:53 | NC | Uji Heat Rate Pasca OH | 9999 Total unit performance testing (use appropriate codes for individual component testing) - Performance - Performance | F790 Testing | Pengujian Heat Rate beban 50% dan 85% | 39.402 | 36 | 2024-10-22 18:00 | Derating | 25.598 | 18 | 0 day 10:07 | 10.1167 | 3.9841 | 3.3722 | 258.9664 | 182.1 |  | 10 | 77
2024-10-22 18:00 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-10-23 06:30 | Derating | 5.897 | 0 | 0 day 12:30 | 12.5 | 1.134 | 0 | 73.7125 | 0 |  | 10 | 78
2024-10-23 06:30 | NC | Uji Heat Rate Pasca OH | 9999 Total unit performance testing (use appropriate codes for individual component testing) - Performance - Performance | F790 Testing | Pengujian Heat Rate beban 75% dan 100% | 51.4087 | 46.97 | 2024-10-23 12:30 | Derating | 13.5913 | 7.03 | 0 day 6:00 | 6 | 1.2546 | 0.78111 | 81.548 | 42.18 |  | 10 | 79
2024-10-23 12:30 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-11-01 | Derating | 5.897 | 0 | 8 day 11:30 | 203.5 | 18.4621 | 0 | 1200.0395 | 0 |  | 10 | 80
2024-11-01 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.2596 | 54 | 2024-11-23 11:00 | Derating | 5.7404 | 0 | 22 day 11:00 | 539 | 47.6012 | 0 | 3094.0756 | 0 |  | 11 | 81
2024-11-23 11:00 | FD | Kendala Perfoma BFP 2A | 3410 Feedwater pump - Feedwater System - Balance of Plant | F790 Testing | Change Over kembali ke BFP 2B | 54.0689 | 49.27 | 2024-11-23 14:04 | Derating | 10.9311 | 4.73 | 0 day 3:04 | 3.0667 | 0.51572 | 0.26862 | 33.522 | 14.5053 |  | 11 | 82
2024-11-23 14:04 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.2596 | 54 | 2024-12-01 | Derating | 5.7404 | 0 | 7 day 9:56 | 177.9333 | 15.714 | 0 | 1021.4085 | 0 |  | 11 | 83
2024-12-01 | MD | Isu Pemotongan Blade Row 15 Turbin MSV dan CV tidak full open, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.2704 | 54 | 2024-12-01 12:00 | Derating | 5.7296 | 0 | 0 day 12:00 | 12 | 1.0578 | 0 | 68.7552 | 0 |  | 12 | 84
2024-12-01 12:00 | FD | Load Control Maximal, Isu Control Valve tidak full open | 4261 Control valves - Valves - Steam Turbine | F090 Calibration, not within limits | Inspeksi pada saat OH dan uji karakteristik | 55.9886 | 51.01 | 2024-12-01 23:00 | Derating | 9.0114 | 2.99 | 0 day 11:00 | 11 | 1.525 | 0.60907 | 99.1257 | 32.89 |  | 12 | 85
2024-12-01 23:00 | MD | Isu Pemotongan Blade Row 15 Turbin MSV dan CV tidak full open, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.2704 | 54 | 2025-01-01 | Derating | 5.7296 | 0 | 30 day 1:00 | 721 | 63.5545 | 0 | 4131.0416 | 0 |  | 12 | 86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 221
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 222
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 223
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 224
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 225
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 226
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 227
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 228
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 229
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 230
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 231
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 232
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 233
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 234
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 235
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 236
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 237
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 238
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 239
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 240
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 241
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 242
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 243
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 244
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 245
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 246
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 247
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 248
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 249
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 250
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 251
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 252
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 253
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 254
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 255
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 256
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 257
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 258
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 259
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 260
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 261
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 262
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 263
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 264
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 265
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 266
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 267
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 268
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 269
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 270
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 271
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 272
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 273
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 274
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 275
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 276
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 277
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 278
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 279
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 280
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 281
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 282
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 283
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 284
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 285
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 286
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 287
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 288
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 289
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 290
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 291
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 292
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 293
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 294
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 295
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 296
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 297
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 298
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 299
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 300
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 301
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 302
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 303
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 304
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 305
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 306
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 307
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 308
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 309
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 310
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 311
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 312
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 313
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 314
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 315
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 316
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 317
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 318
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 319
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 320
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 321
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 322
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 323
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 324
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 325
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 326
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 327
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 328
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 329
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 330
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 331
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 332
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 333
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 334
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 335
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 336
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 337
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 338
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 339
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 340
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 341
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 342
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 343
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 344
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 345
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 346
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 347
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 348
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 349
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 350
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 351
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 352
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 353
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 354
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 355
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 356
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 357
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 358
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 359
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 360
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 361
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 362
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 363
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 364
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 365
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 366
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 367
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 368
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 369
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 370
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 371
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 372
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 373
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 374
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 375
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 376
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 377
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 378
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 379
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 380
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 381
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 382
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 383
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 384
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 385
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 386
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 387
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 388
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 389
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 390
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 391
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 392
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 393
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 394
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 395
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 396
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 397
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 398
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 399
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 400
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 401
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 402
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 403
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 404
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 405
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 406
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 407
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 408
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 409
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 410
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 411
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 412
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 413
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 414
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 415
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 416
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 417
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 418
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 419
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 420
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 421
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 422
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 423
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 424
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 425
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 426
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 427
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 428
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 429
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 430
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 431
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 432
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 433
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 434
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 435
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 436
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 437
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 438
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 439
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 440
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 441
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 442
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 443
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 444
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 445
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 446
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 447
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 448
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 449
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 450
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 451
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 452
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 453
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 454
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 455
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 456
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 457
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 458
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 459
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 460
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 461
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 462
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 463
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 464
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 465
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 466
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 467
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 468
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 469
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 470
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 471
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 472
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 473
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 474
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 475
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 476
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 477
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 478
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 479
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 480
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 481
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 482
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 483
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 484
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 485
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 486
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 487
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 488
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 489
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 490
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 491
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 492
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 493
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 494
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 495
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 496
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 497
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 498
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 499
[6 empty] | 0 |  |  |  | 65 |  | 0 day 0:00 | 0 | 0 |  | 0 | #VALUE! |  |  | 500

## EFOR
2024-02-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 52.52 | 47.09 | 2024-02-01 13:20 | Derating | 12.48 | 6.91 | 0 day 13:20 | 13.33 | 2.56 | 1.71 | 166.34 | 92.13
2024-02-01 15:15 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.46 | 49.72 | 2024-02-09 03:00 | Derating | 9.54 | 4.28 | 7 day 11:45 | 179.75 | 26.39 | 14.25 | 1715.23 | 769.33
2024-02-09 07:25 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.87 | 49.19 | 2024-02-09 22:14 | Derating | 10.13 | 4.81 | 0 day 14:49 | 14.82 | 2.31 | 1.32 | 150.14 | 71.27
2024-02-10 10:07 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.9 | 49.22 | 2024-02-10 22:55 | Derating | 10.1 | 4.78 | 0 day 12:48 | 12.8 | 1.99 | 1.13 | 129.28 | 61.18
2024-02-11 10:21 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.27 | 49.55 | 2024-02-11 23:05 | Derating | 9.73 | 4.45 | 0 day 12:44 | 12.73 | 1.91 | 1.05 | 123.92 | 56.66
2024-02-12 09:46 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.08 | 49.38 | 2024-02-12 23:05 | Derating | 9.92 | 4.62 | 0 day 13:19 | 13.32 | 2.03 | 1.14 | 132.12 | 61.52
2024-02-13 08:13 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.17 | 49.46 | 2024-02-14 01:02 | Derating | 9.83 | 4.54 | 0 day 16:49 | 16.82 | 2.54 | 1.41 | 165.35 | 76.35
2024-02-14 11:15 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.54 | 48.9 | 2024-02-15 21:52 | Derating | 10.46 | 5.1 | 1 day 10:37 | 34.62 | 5.57 | 3.27 | 361.98 | 176.55
2024-02-16 01:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.53 | 48.89 | 2024-02-25 06:35 | Derating | 10.47 | 5.11 | 9 day 5:05 | 221.08 | 35.6 | 20.92 | 2314.32 | 1129.74
2024-02-25 08:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.16 | 48.56 | 2024-02-26 02:55 | Derating | 10.84 | 5.44 | 0 day 18:25 | 18.42 | 3.07 | 1.86 | 199.57 | 100.19
2024-02-26 07:45 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.43 | 48.8 | 2024-02-26 13:23 | Derating | 10.57 | 5.2 | 0 day 5:38 | 5.63 | 0.92 | 0.54 | 59.54 | 29.29
2024-02-26 21:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 53.91 | 48.33 | 2024-02-26 22:49 | Derating | 11.09 | 5.67 | 0 day 1:19 | 1.32 | 0.22 | 0.14 | 14.61 | 7.47
2024-02-27 08:00 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.28 | 49.56 | 2024-02-28 02:30 | Derating | 9.72 | 4.44 | 0 day 18:30 | 18.5 | 2.77 | 1.52 | 179.83 | 82.14
2024-02-28 08:03 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.82 | 49.15 | 2024-02-29 07:00 | Derating | 10.18 | 4.85 | 0 day 22:57 | 22.95 | 3.59 | 2.06 | 233.59 | 111.31
2024-02-29 07:41 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.11 | 49.41 | 2024-03-01 | Derating | 9.89 | 4.59 | 0 day 16:19 | 16.32 | 2.48 | 1.39 | 161.34 | 74.89
2024-03-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.53 | 49.52 | 2024-03-02 06:56 | Derating | 10.47 | 4.48 | 1 day 6:56 | 30.93 | 4.98 | 2.57 | 323.83 | 138.58
2024-03-02 08:45 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.46 | 50.36 | 2024-03-30 06:18 | Derating | 9.54 | 3.64 | 27 day 21:33 | 669.55 | 98.31 | 45.13 | 6389.9 | 2437.16
2024-03-30 07:40 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.19 | 50.12 | 2024-04-01 | Derating | 9.81 | 3.88 | 1 day 16:20 | 40.33 | 6.09 | 2.9 | 395.58 | 156.49
2024-04-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.31 | 50.23 | 2024-04-09 23:40 | Derating | 9.69 | 3.77 | 8 day 23:40 | 215.67 | 32.14 | 15.06 | 2089.1 | 813.06
2024-04-15 07:40 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.61 | 49.59 | 2024-04-26 15:55 | Derating | 10.39 | 4.41 | 11 day 8:15 | 272.25 | 43.52 | 22.23 | 2829.08 | 1200.62
2024-04-30 08:20 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.2 | 49.22 | 2024-05-01 | Derating | 10.8 | 4.78 | 0 day 15:40 | 15.67 | 2.6 | 1.39 | 169.18 | 74.89
2024-05-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.52 | 49.48 | 2024-05-05 01:05 | Derating | 10.48 | 4.52 | 4 day 1:05 | 97.08 | 15.66 | 8.13 | 1017.72 | 438.82
[15 empty] | 2024 | EFOR Total | 8159.64 | MWh
(E(FOH + EFDH) x DMNJ / E(FOH+SH+EFHRS) * DMN * 100%
Dik :
[13 empty] | FOH | 0
[13 empty] | EFDH | 151.1044 | Jam
[13 empty] | SH | 8608.8956 | Jam
[13 empty] | EFDHRS | 0 | Jam
[13 empty] | DMN | 54000 | Kw
[13 empty] | EFOR | 1.755%

## EAF
2024-01-01 05:00 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.6646 | 54 | 2024-01-26 09:33 | Derating | 5.3354 | 0 | 25 day 4:33 | 604.55 | 49.6233 | 0 | 3225.5161 | 0
2024-01-26 11:10 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.6646 | 54 | 2024-02-01 | Derating | 5.3354 | 0 | 5 day 12:50 | 132.8333 | 10.9034 | 0 | 708.719 | 0
2024-02-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 52.5242 | 47.09 | 2024-02-01 13:20 | Derating | 12.4758 | 6.91 | 0 day 13:20 | 13.3333 | 2.5591 | 1.7062 | 166.3442 | 92.1333
2024-02-01 15:15 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.4577 | 49.72 | 2024-02-09 03:00 | Derating | 9.5423 | 4.28 | 7 day 11:45 | 179.75 | 26.3882 | 14.2469 | 1715.2306 | 769.33
2024-02-09 07:25 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.8665 | 49.19 | 2024-02-09 22:14 | Derating | 10.1335 | 4.81 | 0 day 14:49 | 14.8167 | 2.3099 | 1.3198 | 150.1443 | 71.2682
2024-02-10 10:07 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.9 | 49.22 | 2024-02-10 22:55 | Derating | 10.1 | 4.78 | 0 day 12:48 | 12.8 | 1.9889 | 1.133 | 129.2802 | 61.184
2024-02-11 10:21 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.2681 | 49.55 | 2024-02-11 23:05 | Derating | 9.7319 | 4.45 | 0 day 12:44 | 12.7333 | 1.9065 | 1.0493 | 123.9199 | 56.6633
2024-02-12 09:46 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.0785 | 49.38 | 2024-02-12 23:05 | Derating | 9.9215 | 4.62 | 0 day 13:19 | 13.3167 | 2.0326 | 1.1393 | 132.1219 | 61.523
2024-02-13 08:13 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.1677 | 49.46 | 2024-02-14 01:02 | Derating | 9.8323 | 4.54 | 0 day 16:49 | 16.8167 | 2.5438 | 1.4138 | 165.3468 | 76.3477
2024-02-14 11:15 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.5431 | 48.9 | 2024-02-15 21:52 | Derating | 10.4569 | 5.1 | 1 day 10:37 | 34.6167 | 5.569 | 3.2694 | 361.9844 | 176.545
2024-02-16 01:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.5319 | 48.89 | 2024-02-25 06:35 | Derating | 10.4681 | 5.11 | 9 day 5:05 | 221.0833 | 35.6049 | 20.921 | 2314.3211 | 1129.7358
2024-02-25 08:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.1638 | 48.56 | 2024-02-26 02:55 | Derating | 10.8362 | 5.44 | 0 day 18:25 | 18.4167 | 3.0702 | 1.8553 | 199.5662 | 100.1867
2024-02-26 07:45 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.4315 | 48.8 | 2024-02-26 13:23 | Derating | 10.5685 | 5.2 | 0 day 5:38 | 5.6333 | 0.91593 | 0.54247 | 59.5358 | 29.2933
2024-02-26 21:30 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 53.9073 | 48.33 | 2024-02-26 22:49 | Derating | 11.0927 | 5.67 | 0 day 1:19 | 1.3167 | 0.2247 | 0.13825 | 14.6054 | 7.4655
2024-02-27 08:00 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.2792 | 49.56 | 2024-02-28 02:30 | Derating | 9.7208 | 4.44 | 0 day 18:30 | 18.5 | 2.7667 | 1.5211 | 179.8344 | 82.14
2024-02-28 08:03 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.8219 | 49.15 | 2024-02-29 07:00 | Derating | 10.1781 | 4.85 | 0 day 22:57 | 22.95 | 3.5936 | 2.0612 | 233.5872 | 111.3075
2024-02-29 07:41 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.1119 | 49.41 | 2024-03-01 | Derating | 9.8881 | 4.59 | 0 day 16:19 | 16.3167 | 2.4822 | 1.3869 | 161.3406 | 74.8935
2024-03-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.5314 | 49.52 | 2024-03-02 06:56 | Derating | 10.4686 | 4.48 | 1 day 6:56 | 30.9333 | 4.982 | 2.5663 | 323.828 | 138.5813
2024-03-02 08:45 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.4564 | 50.36 | 2024-03-30 06:18 | Derating | 9.5436 | 3.64 | 27 day 21:33 | 669.55 | 98.3061 | 45.1326 | 6389.896 | 2437.162
2024-03-30 07:40 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.1921 | 50.12 | 2024-04-01 | Derating | 9.8079 | 3.88 | 1 day 16:20 | 40.3333 | 6.0859 | 2.898 | 395.5835 | 156.4933
2024-04-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 55.3133 | 50.23 | 2024-04-09 23:40 | Derating | 9.6867 | 3.77 | 8 day 23:40 | 215.6667 | 32.1401 | 15.0567 | 2089.1035 | 813.0633
2024-04-15 07:40 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.6085 | 49.59 | 2024-04-26 15:55 | Derating | 10.3915 | 4.41 | 11 day 8:15 | 272.25 | 43.5244 | 22.2337 | 2829.0837 | 1200.6225
2024-04-30 08:20 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.2011 | 49.22 | 2024-05-01 | Derating | 10.7989 | 4.78 | 0 day 15:40 | 15.6667 | 2.6028 | 1.3868 | 169.1833 | 74.8867
2024-05-01 | FD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 54.5171 | 49.48 | 2024-05-05 01:05 | Derating | 10.4829 | 4.52 | 4 day 1:05 | 97.0833 | 15.6572 | 8.1262 | 1017.7184 | 438.8167
2024-05-05 01:05 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max dan Main Steam di batasi 83 Bar terkait mitigasi kebocoran pipa | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.4972 | 54 | 2024-05-13 | Derating | 5.5028 | 0 | 7 day 22:55 | 190.9167 | 16.1627 | 0 | 1050.5762 | 0
2024-09-27 18:00 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.3244 | 54 | 2024-10-01 | Derating | 5.6756 | 0 | 3 day 6:00 | 78 | 6.8107 | 0 | 442.6968 | 0
2024-10-01 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-10-02 11:27 | Derating | 5.897 | 0 | 1 day 11:27 | 35.45 | 3.2161 | 0 | 209.0486 | 0
2024-10-02 19:00 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-10-20 07:09 | Derating | 5.897 | 0 | 17 day 12:09 | 420.15 | 38.1173 | 0 | 2477.6246 | 0
2024-10-20 14:07 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-10-22 07:53 | Derating | 5.897 | 0 | 1 day 17:46 | 41.7667 | 3.7892 | 0 | 246.298 | 0
2024-10-22 18:00 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-10-23 06:30 | Derating | 5.897 | 0 | 0 day 12:30 | 12.5 | 1.134 | 0 | 73.7125 | 0
2024-10-23 12:30 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.103 | 54 | 2024-11-01 | Derating | 5.897 | 0 | 8 day 11:30 | 203.5 | 18.4621 | 0 | 1200.0395 | 0
2024-11-01 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.2596 | 54 | 2024-11-23 11:00 | Derating | 5.7404 | 0 | 22 day 11:00 | 539 | 47.6012 | 0 | 3094.0756 | 0
2024-11-23 14:04 | MD | Isu Pemotongan Blade Row 15 Turbin, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.2596 | 54 | 2024-12-01 | Derating | 5.7404 | 0 | 7 day 9:56 | 177.9333 | 15.714 | 0 | 1021.4085 | 0
2024-12-01 | MD | Isu Pemotongan Blade Row 15 Turbin MSV dan CV tidak full open, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.2704 | 54 | 2024-12-01 12:00 | Derating | 5.7296 | 0 | 0 day 12:00 | 12 | 1.0578 | 0 | 68.7552 | 0
2024-12-01 23:00 | MD | Isu Pemotongan Blade Row 15 Turbin MSV dan CV tidak full open, Load Control Max | 4212 Buckets or blades - Low Pressure Turbine - Steam Turbine | F060 Broken | Reblading Saat OH | 59.2704 | 54 | 2025-01-01 | Derating | 5.7296 | 0 | 30 day 1:00 | 721 | 63.5545 | 0 | 4131.0416 | 0
[16 empty] | EAF Total | 8159.64
≤ (AH-EPDH-EUDH-ESDH) DMN) / E (PH x DMN) × 100%
Dik
[14 empty] | AH | 8760 | Jam
[14 empty] | EPDH | 0 | Jam | Yg Biru, kenapa 0
[14 empty] | EUDH | 151.1044 | Jam
[14 empty] | ESDH | 0 | Jam
[14 empty] | DMN | 54000 | Kw
[14 empty] | PH | 8760 | Jam
[14 empty] | EAF | 98.28%
[14 empty] | Mempengaruhi EAF | 1.725%
[14 empty] | Total Kerugian | 9791568000 |  | Untung pertahun
Resiko sebelum pengadaan material atau sesudah pengadaan material

## Efisiensi
Equipment name | 2024 |  | EFOR | EAF |  | EFOR | EAF | 2028 |  |  |  | EFOR | EAF | 2029 |  |  |  | EFOR | EAF | 2030 |  |  |  | EFOR | EAF
| NPHR | EFDH |  |  | MOH |  |  | FOH | EFDH | EMDH | MOH |  |  | FOH | EFDH | EMDH | MOH |  |  | FOH | EFDH | EMDH | MOH
Blade Turbine unit 2 | 10203499727 | 151 | 1.76% | 1.72%

## Heatmap
Nilai Investasi | 5955150000 | Rp
Potensi penghematan / saving / keuntungan | 815964000 | Rp/bulan
| 9791568000 | RP/tahun | [5 empty] | Loss | 11520000
Discount rate bank per tahun | 9.71% | % | asumsi |  |  |  |  | BPP | 903
Manfaat aset investasi | 1 | tahun | asumsi |  |  |  |  | TP | 1234
Perhitungan Finansial | [7 empty] | CF | 0.73
Rate per tahun | 9.71% |  | (9.28% per tahun) |  |  |  |  | Saving | 2783577600
Investasi | -5955150000 | [6 empty] | TOTAL | 3083577600
Tahun-1 | 9791568000 |  | 2969804881.05 | =NPV(B8;B10)+B9 | 1 | =IF(D10>0;1;0)
Tahun-2 | 9791568000 |  | 11104847157.096 | =NPV(B$8;B$10:B11)+B$9 | 1 | =IF(D11>0;1;0) |  | Penggantian komponen peralatan karena gagal pelumasan
Tahun-3 | 9791568000 |  | 18519888881.6845 | =NPV(B$8;B$10:B12)+B$9 | 1 | =IF(D12>0;1;0)
Tahun-4 | 9791568000 |  | 25278654467.8557 | =NPV(B$8;B$10:B13)+B$9 | 1 | =IF(D13>0;1;0) |  |  | 300000000
Tahun-5 | 9791568000 |  | 31439228331.8345 | =NPV(B$8;B$10:B14)+B$9 | 1 | =IF(D14>0;1;0)
Tahun-6 | 9791568000 |  | 37054554066.9351 | =NPV(B$8;B$10:B15)+B$9 | 1 | =IF(D15>0;1;0)
Tahun-7 | 9791568000 |  | 42172889437.5491 | =NPV(B$8;B$10:B16)+B$9 | 1 | =IF(D16>0;1;0)
Tahun-8 | 9791568000 |  | 46838221103.4082 | =NPV(B$8;B$10:B17)+B$9 | 1 | =IF(D17>0;1;0)
Tahun-9 | 9791568000 |  | 51090642638.2355 | =NPV(B$8;B$10:B18)+B$9 | 1 | =IF(D18>0;1;0)
Tahun-10 | 9791568000 |  | 54966699091.4552 | =NPV(B$8;B$10:B19)+B$9 | 1 | =IF(D19>0;1;0)
Tahun | Saving/tahun |  | NPV |  | 10
PARAMATER FINANSIAL KKP
IRR | = | % | 164.4% | =IRR(B9:C19) |  | Layak | >16%
PP | = | tahun | 1 | =IF((10-F20+1)>10;"10";10-F20+1&" ") |  | Layak | < masa manfaat aset
B/C | = | kali | 16.4422 | =SUM(B10:B19)/-B9 |  | Layak | >1
NPV | = | Rp | 54966699091.4552 | =NPV(B$8;B$10:B19)+B$9 |  | Layak | ( + )
KESIMPULAN |  |  | LAYAK

## Matriks Resiko
No | PROSES BISNIS | KEJADIAN RISIKO | PENYEBAB | KONTROL EKSISTING | LEVEL RISIKO | No | PROSES BISNIS | KEJADIAN RISIKO | PENYEBAB | KONTROL EKSISTING | LEVEL RISIKO
[5 empty] | RESIDU | [5 empty] | RESIDU
1 | PERENCANAAN | Terjadi Kesalahan Desain | Perencanaan teknis yang kurang matang | Proses review dan validasi desain oleh tim teknis dan QC sebelum implementasi | Tinggi (3, C) | 1 | PERENCANAAN | Terjadi Kesalahan Desain | Perencanaan teknis yang kurang matang | Proses review dan validasi desain oleh tim teknis dan QC sebelum implementasi | Tinggi (3, C)
2 |  | Tindakan Kecurangan | Lemahnya sistem kontrol internal dan kurangnya budaya kepatuhan | Kebijakan anti-fraud, dan sistem pelaporan whistleblowing | Tinggi (3, C) | 2 |  | Tindakan Kecurangan | Lemahnya sistem kontrol internal dan kurangnya budaya kepatuhan | Kebijakan anti-fraud, dan sistem pelaporan whistleblowing | Tinggi (3, C)
3 | PENGADAAN | Gagal Pengadaan | Keterbatasan vendor dan kesalahan dalam spesifikasi atau scope pekerjaan | Evaluasi vendor yang ketat oleh tim pengadaan | Tinggi (3, C) | 3 | PENGADAAN | Gagal Pengadaan | Keterbatasan vendor dan kesalahan dalam spesifikasi atau scope pekerjaan | Evaluasi vendor yang ketat oleh tim pengadaan | Tinggi (3, C)
4 |  | Terjadi Dispute pada Kontrak | Klausul kontrak yang tidak jelas, kurangnya pemahaman terhadap isi kontrak, perbedaan interpretasi kontrak | Penggunaan kontrak standar dengan klausul penyelesaian sengketa | Tinggi (3, C) | 4 |  | Terjadi Dispute pada Kontrak | Klausul kontrak yang tidak jelas, kurangnya pemahaman terhadap isi kontrak, perbedaan interpretasi kontrak | Penggunaan kontrak standar dengan klausul penyelesaian sengketa | Tinggi (3, C)
5 | PELAKSANAAN | Waktu Penyelesaian Pekerjaan Terlambat. | Kurangnya manajemen proyek yang efektif / keterlambatan pasokan material / kurangnya tenaga kerja | Sistem pemantauan pekerjaan dan pelaporan progres berkala | Tinggi (3, C) | 5 | PELAKSANAAN | Waktu Penyelesaian Pekerjaan Terlambat. | Kurangnya manajemen proyek yang efektif / keterlambatan pasokan material / kurangnya tenaga kerja | Sistem pemantauan pekerjaan dan pelaporan progres berkala | Tinggi (3, C)
6 |  | Delivery Barang Terlambat | Masalah logistik, keterlambatan produksi dari pemasok, dan gangguan eksternal seperti cuaca buruk | Jadwal logistik yang ketat dan perencanaan buffer waktu | Tinggi (3, C) | 6 |  | Delivery Barang Terlambat | Masalah logistik, keterlambatan produksi dari pemasok, dan gangguan eksternal seperti cuaca buruk | Jadwal logistik yang ketat dan perencanaan buffer waktu | Tinggi (3, C)
7 |  | Laporan Pekerjaan Tidak Lengkap | Kurangnya sistem pelaporan dan pengawasan yang standar | Format standar laporan dengan checklist yang telah ditetapkan | Tinggi (3, C) | 7 |  | Laporan Pekerjaan Tidak Lengkap | Kurangnya sistem pelaporan dan pengawasan yang standar | Format standar laporan dengan checklist yang telah ditetapkan | Tinggi (3, C)
8 |  | Terjadi Kecelakaan Kerja | Tidak menggunakan APD atau kurangnya kepatuhan terhadap prosedur keselamatan | Briefing K3 sebelum memulai pekerjaan dan penggunaan APD (Alat Pelindung Diri) yang diwajibkan | Tinggi (3, C) | 8 |  | Terjadi Kecelakaan Kerja | Tidak menggunakan APD atau kurangnya kepatuhan terhadap prosedur keselamatan | Briefing K3 sebelum memulai pekerjaan dan penggunaan APD (Alat Pelindung Diri) yang diwajibkan | Tinggi (3, C)
9 | TESTING/COMMISSIONING | Keterlambatan jadwal komisioning | Kurangnya koordinasi antara tim proyek dan vendor, keterlambatan dalam persiapan teknis | Timeline proyek dengan milestone yang jelas dan evaluasi berkala | Tinggi (3, C) | 9 | TESTING/COMMISSIONING | Keterlambatan jadwal komisioning | Kurangnya koordinasi antara tim proyek dan vendor, keterlambatan dalam persiapan teknis | Timeline proyek dengan milestone yang jelas dan evaluasi berkala | Tinggi (3, C)
10 |  | Hasil komisioning tidak sesuai dengan standar keberterimaan (Kontraktual) | Kesalahan dalam perakitan atau instalasi | SOP pengujian dan validasi hasil komisioning | Tinggi (3, C) | 10 |  | Hasil komisioning tidak sesuai dengan standar keberterimaan (Kontraktual) | Kesalahan dalam perakitan atau instalasi | SOP pengujian dan validasi hasil komisioning | Tinggi (3, C)
11 |  | Hasil performance test tidak sesuai ketentuan kontraktual | Parameter pengujian tidak sesuai | Pengujian berulang sebelum penerimaan akhir proyek | Tinggi (3, C) | 11 |  | Hasil performance test tidak sesuai ketentuan kontraktual | Parameter pengujian tidak sesuai | Pengujian berulang sebelum penerimaan akhir proyek | Tinggi (3, C)
12 | SERAH TERIMA BA | Salah satu pihak gagal untuk memenuhi persyaratan kontrak | Kegagalan dalam manajemen kontrak, kurangnya sanksi tegas | Penggunaan kontrak standar dengan klausul penalti dan denda keterlambatan. | Tinggi (3, C) | 12 | SERAH TERIMA BA | Salah satu pihak gagal untuk memenuhi persyaratan kontrak | Kegagalan dalam manajemen kontrak, kurangnya sanksi tegas | Penggunaan kontrak standar dengan klausul penalti dan denda keterlambatan. | Tinggi (3, C)
13 | PEMBAYARAN | Pembayaran Tagihan Pihak Ketiga Terlambat | Kurangnya komunikasi antara user, keuangan dan penyedia | Sistem pembayaran terjadwal dan pemantauan yang ketat | Tinggi (3, C) | 13 | PEMBAYARAN | Pembayaran Tagihan Pihak Ketiga Terlambat | Kurangnya komunikasi antara user, keuangan dan penyedia | Sistem pembayaran terjadwal dan pemantauan yang ketat | Tinggi (3, C)
12
1
2
Risiko Residu
Risiko Target
Keterangan :
3
7
8
5
6
9
10
11
12
13

## NPHR
NPHR Bulanan | Satuan | 2022 | [12 empty] | NPHR Kumulatif | Satuan | 2022
|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  |  | Jan | s.d Feb | s.d Mar | s.d Apr | s.d May | s.d Jun | s.d Jul | s.d Aug | s.d Sep | s.d Oct | s.d Nov | s.d Dec
Unit 1 | kCal/kWh | 3805.3317 | 3477.0503 | 3495.125 | 3559.2215 | 3568.5796 | 3780.3972 | 3743.5294 | 3563.4104 | 3674.2651 | 3501.1551 | 3557.6645 | 3630.9849 |  | Unit 1 | kCal/kWh | 3805.3317 | 3611.1735 | 3567.219 | 3565.2646 | 3566.0071 | 3584.8266 | 3598.8724 | 3593.4661 | 3602.2583 | 3590.2063 | 3587.092 | 3588.7978
Unit 2 | kCal/kWh | 3447.5582 | 3414.3587 | 3418.0745 | 3395.3852 | 3536.436 | 3433.6163 | 3445.214 | 3545.0158 | 3457.3133 | 3566.8404 | 3559.2946 | 3440.1007 |  | Unit 2 | kCal/kWh | 3447.5582 | 3431.3413 | 3426.648 | 3419.7243 | 3439.2454 | 3438.3164 | 3439.3779 | 3451.7514 | 3452.3804 | 3463.405 | 3468.0626 | 3465.3999
NPHR Bulanan | Satuan | 2022 Jan: 2023 |  | NPHR Kumulatif | Satuan | 2023
|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  |  | Jan | s.d Feb | s.d Mar | s.d Apr | s.d May | s.d Jun | s.d Jul | s.d Aug | s.d Sep | s.d Oct | s.d Nov | s.d Dec
Unit 1 | kCal/kWh | 3480.4933 | 3484.151 | 3613.0967 | 3571.6765 | 3480.4067 | 3528.1808 | 3537.0412 | 3487.6966 | 3441.5663 | 3604.3398 | 3335.7287 | 3357.6607 |  | Unit 1 | kCal/kWh | 3480.4933 | 3482.2403 | 3511.2446 | 3526.9475 | 3516.7212 | 3518.7717 | 3521.7103 | 3516.9215 | 3507.7885 | 3517.7452 | 3500.7883 | 3487.8913
Unit 2 | kCal/kWh | 3390.0312 | 3402.6323 | 3532.48 | 3648.6817 | 3776.1038 | 3707.121 | 3842.5124 | 3800.9715 | 3614.262 | 3700.445 | 3554.6018 | 3402.8988 |  | Unit 2 | kCal/kWh | 3390.0312 | 3395.5086 | 3444.8842 | 3477.3033 | 3493.474 | 3540.2117 | 3590.4344 | 3623.4378 | 3622.2702 | 3631.5687 | 3623.8972 | 3607.7007
NPHR Bulanan | Satuan | 2023 Jan: 2024 |  | NPHR Kumulatif | Satuan | 2024
|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  |  | Jan | s.d Feb | s.d Mar | s.d Apr | s.d May | s.d Jun | s.d Jul | s.d Aug | s.d Sep | s.d Oct | s.d Nov | s.d Dec
Unit 1 | kCal/kWh | 3399.2247 |  | 0 | 3760.0827 | 3440.3361 | 3582.2216 | 3417.4241 | 3440.9411 | 3324.1405 | 3516.7961 | 3548.8609 | 3472.0704 |  | Unit 1 | kCal/kWh | 3399.2247 | 3405.5716 | 3879.1067 | 3840.7286 | 3548.761 | 3562.8379 | 3519.5536 | 3501.6319 | 3469.6275 | 3477.193 | 3486.2062 | 3484.5063
Unit 2 | kCal/kWh | 3467.9424 | 3519.9717 | 3540.3767 | 3653.1033 | 3675.754 | 3764.1663 | 3637.7601 |  | 3573.2061 | 3749.5251 | 3764.2007 | 3628.3229 |  | Unit 2 | kCal/kWh | 3467.9424 | 3492.5204 | 3509.1317 | 3542.6324 | 3570.0497 | 3602.4783 | 3607.0929 | 3607.0928 | 3604.7737 | 3623.1961 | 3638.7192 | 3637.6922
[15 empty] | NPHR | TAHUN
[16 empty] | 2022 | 2023 | 2024
[15 empty] | Unit 2 | 3465.3999 | 3607.7007 | 3637.6922
[15 empty] | NPHR | 172.2923 | kCal/kWh
Jika
[15 empty] | kWh Unit 2 | 382670530.81
[15 empty] | 172.29 | kCal/kWh | 382670531.81 | kWh
[15 empty] | kCal | 65930305925.5449
[14 empty] | 4200 | kCal/kg | 65930305926 | kCal
[15 empty] | kg | 15697691.8871
[15 empty] | HBB (Rp) /Kg | 650
[15 empty] | Loss NPHR | 10203499726.6429