## General
Study ID | Untitled
Study Case ID | LF
Data Revision | Base
Configuration | Normal
Loading Cat | Design
Generation Cat | Design
Diversity Factor | Normal Loading
Buses | 7
Branches | 6
Generators | 0
Power Grids | 1
Loads | 1
Load-MW | 10,055
Load-Mvar | 6,231
Generation-MW | 10,37
Generation-Mvar | 7,789
Loss-MW | 0,315
Loss-Mvar | 1,558
Mismatch-MW | 0
Mismatch-Mvar | 0

## Bus
Bus ID | Nominal kV | Voltage | MW Loading | Mvar Loading | Amp Loading
Bus GI-20kV | 20 | 20,811 | 10,362 | 7,439 | 353,9
Bus GI 150kV | 150 | 150 | 10,37 | 7,789 | 49,92
CUBICLE INCOMING | 20 | 20,249 | 10,105 | 7,234 | 354,3
CUBICLE OUTGOING | 20 | 20,249 | 10,105 | 7,234 | 354,3
LVMDP PELANGGAN | 0,4 | 0,385 | 10,055 | 6,231 | 17717
TM-11 | 20 | 20,752 | 10,336 | 7,424 | 354
TM-11' | 20 | 20,291 | 10,124 | 7,246 | 354,2

## Branch
ID | Bus 1 | Bus 2 | Type | Rating 1 | kW Flow | kvar Flow | Amp Flow | % PF | % Loading | % Voltage Drop | kW Losses | kvar Losses
Cable XLPE-1 | Bus GI-20kV | TM-11 | Cable | 280 m | 10335,5 | 7424,1 | 354 | 81,22 |  | 0,29 | 26,52 | 14,99
Cable XLPE-2 | TM-11' | CUBICLE INCOMING | Cable | 200 m | 10104,7 | 7234,4 | 354,3 | 81,31 |  | 0,21 | 18,97 | 11,08
SUTM AAAC 150mm | TM-11 | TM-11' | Line | 4820 m | 10123,7 | 7245,5 | 354,2 | 81,32 |  | 2,31 | 211,8 | 178,6
TRAFO PABRIK | CUBICLE OUTGOING | LVMDP PELANGGAN | Transf. 2W | 20 / 0,4 kV | 10104,7 | 7234,4 | 354,3 | 81,31 | 82,8 | 4,88 | 50,16 | 1003,2
TRAFO UTAMA | Bus GI 150kV | Bus GI-20kV | Transf. 2W | 150 / 21,16 kV | 10369,8 | 7789,5 | 49,92 | 79,96 | 21,6 | 1,65 | 7,79 | 350,3

## Load
ID | Rating/Limit | Rated kV | kW | kvar | Amp | % PF | % Loading | Vterminal
PABRIK | 15000 kVA | 0,4 | 10054,5 | 6231,2 | 17717 | 85 | 81,8 | 0,385

## Source
ID | Rating/Limit | Rated kV | MW | Mvar | Amp | % PF
GI BUDURAN | 60 MVA | 150 | 10,37 | 7,789 | 49,92 | 79,96